## Request List
Request# | CAISO# | Start | End | Main Element Impacted | Elements Involved | Path Affected | Work to be Performed | Additional Notes
21-01711 | 15666227 | 02/03/2021 09:00 | 02/28/2030 17:00 | -USBR- GRAND COULEE 287/230KV TRANSFORMER KX-17-A (OLYMPIA-GRAND COULEE NO 1 287KV LINE OPERATING AT 230KV) | OLYMPIA: 287/230KV TRANSFORMER 3, GRAND COULEE: 287/230KV TRANSFORMER 1 | NOEL, RP, SOC, WOCN, IROL, NOH, OKLA | #1421102 -USBR WORK-4 YEAR MAINTENANCE ON TRANSFORMER KX-17-A. LINE RETURNED TO SERVICE AT 230KV | 2-No slimsend date changed to match dart, duplicate authorization voided.
23-04125 | 13016840 | 01/28/2023 17:00 | 09/30/2026 23:59 | ROCKY REACH-MAPLE VALLEY NO 1 345kV LINE OPERATING AT 230KV | ROCKY REACH: 345/230KV TRANSFORMER 1, ROCKY REACH-MAPLE VALLEY NO 1 345kV LINE OPERATING AT 230KV, MAPLE VALLEY: 345/230KV TRANSFORMER 1 | WOCN, SOC/NOEL, CI, GEN, IROL, NOEL, NOH, SOC | ROCKY REACH-MAPLE VALLEY 1 345KV LINE OPERATING AT 230KV DUE TO MAPLE VALLEY 345/230KV BANK 1 GASSING
23-16749 |  | 10/26/2023 07:00 | 03/28/2025 16:00 | VALHALLA: B-280 TERMINAL OF THE VALHALLA-CHELAN CO PUD 115KV FEEDER T1 | VALHALLA: B-280 TERMINAL OF THE VALHALLA-CHELAN CO PUD 115KV FEEDER T1, VALHALLA: CHELAN CO PUD 115KV FEEDER T1 | CI | THEIR WORK. ADD NITROGEN TO BANK 1 | OPS CAN SUPPORTEQUIPMENT ALREADY REPORTED OUT ON 23-08577
23-18445 | 14853282 | 12/14/2023 06:40 | 03/31/2025 16:00 | BCH - CHAPMAN: 5CX1 | BCH - CHAPMAN: 5CX1 | NI | BCH: THEIR WORK
23-18564 | 14980739 | 12/20/2023 14:56 | 12/31/2024 16:00 | PACW - BURNS: 500KV SERIES CAP SAGMENT 1 & 2 | PACW - BURNS: 500KV SERIES CAP SAGMENT 1 & 2, BURNS: 500KV SERIES CAP SEGMENT 1, BURNS: 500KV SERIES CAP SEGMENT 2 | NWACI |  | PACW REMOVED BURNS SERIES CAPS FROM SERVICE DUE TO TROUBLE AT CAPS POSSIBLY CAUSING FAULTS ON HEMINGWAY-SUMMER LAKE 500KV LINE. PACW REPORTS NO ETR FOR BURNS SERIES CAPS AT THIS TIME.
24-11909 | 16116750 | 07/05/2024 17:00 | 12/31/2024 15:00 | MALIN: 500KV REACTOR 2 INCLUDING PCB 4037 | MALIN: PCB 4037, MALIN: 500KV REACTOR 2 | NWACI, COI
24-10059 | 15972235 | 08/15/2024 20:01 | 12/10/2024 17:00 | OLYMPIA: 230/115KV TRANSFORMER 1 INCLUDING PCB'S A-218 AND B-682 | OLYMPIA: 230/115KV TRANSFORMER 1, OLYMPIA: PCB A-218, OLYMPIA: PCB B-682 | NOEL, RP, WOCN, SOC | REPLACE PCB'S A-218 AND B-682 INCLUDING ASSOCIATED DISCONNECTS, EQUIPMENT, WIRING AND SEISMIC UPGRAGES | STATION SERVICE IS FED OFF OF BANK #2ISSUE CLEARANCE ON DO NOT OPERATE TAGSAUX BUS RISERS BETWEEN THE 230KV WEST AUX BUS AND THE A-218 AUX BUS DISCONNECT WERE REMOVED UNDER ITOA# 24-08834
24-13950 |  | 08/16/2024 00:06 | 12/01/2025 17:00 | PG&E - PACIRAS CONTROLLER A |  |  | PG&E WORK-MOVING RAS CIRCUIT FROM THEIR SF CONTROL CENTER TO NEW LOCATION THE FOLLOWING CIRCUITS WILL REMAIN C/O FOR THE DURATION OF THIS OUTAGE: PACIRAS System 1A from Dittmer (INT: 7325 BPA: 7B72) PACIRAS System 2A from Dittmer (INT: 7327 BPA: 7B74) Cut Out RAS DCA (Celilo T/T) at Dittmer (INT: 7323 BPA: 7E62)
24-15500 |  | 09/19/2024 01:00 | 12/11/2024 15:00 | PSE-SHANNON GENERATION
24-13857 | 16375199 | 10/01/2024 08:00 | 12/31/2024 15:00 | -EWEB- COBURG-SPRING CREEK 115KV LINE | COBURG (EWEB)-SPRING CREEK (EWEB) 115KV LINE | EWEB | EWEB RELAY UPGRADE, LINE TO BE OUT FOR DURATION | Spiring Creek PCB 5470 to Coburg PCB 6800 transmission line including the PCB's will be taken out of service.Coburg-Spring Creek 115KV line for relay upgradePRC-002 compliance Spring Creek sub will be restored on 9/24, with the exception of PCB 5470. That breaker will remain isolated, in preparation for this work.See ITOA 24-13344
24-05901 | 15358908 | 10/01/2024 08:00 | 01/30/2025 16:00 | WAPA - TRACY: 500KV SHUNT CAPACITOR PT10A & PT10B | WAPA - TRACY: 500KV SHUNT CAPACITOR PT10A & PT10B | COI | REPLACE SHUNT CAPACITOR BREAKERS 1292 & 1392
24-00047 | 12888891 | 11/01/2024 03:00 | 12/01/2024 21:00 | BIG EDDY-CELILO NO 1 500KV LINE, BIG EDDY-CELILO NO 2 500KV LINE, CELILO-SYLMAR POLE NO 3 1000KV LINE, CELILO-SYLMAR POLE NO 4 1000KV LINE, CELILO: GROUND SWITCH 7939 |  | PDCI, SIG, BGEDY, NWACI | CONTROL OF MOD 4207, 4214, 9084, 9085, AND DISC 7939
24-16571 |  | 11/01/2024 08:00 | 12/01/2024 21:00 | CELILO-SYLMAR POLES 3 & 4 1000KV LINE (GROUNDED) |  |  | LINE MAINTENANCE
24-13394 |  | 11/04/2024 08:00 | 12/06/2024 17:00 | MCNARY: MCNARY-B-1345 SECTION OF MCNARY-BADGER CANYON NO 1 115KV LINE INCLUDING PLYMOUTH TAP TO BC-187 | MCNARY: PCB B-980, MCNARY-B-1345 SECTION OF MCNARY-BADGER CANYON NO 1 115KV LINE, PLYMOUTH TAP TO MCNARY-BADGER CANYON NO 1 115KV LINE | GEN, LOAD, WOM, TCLA | CROSS ARM INSTALLATION AND STRINGING OF CONDUCTOR FROM 1/5-1/12 | CROSS ARM AND CROSS BRACING STRUCTURES 1/6-1/11STRINGING NEW CONDUCTOR FROM STRUCTURE 1/5-1/12CLEARANCE LIMITS:B-1345 LSD, BENTON PUD'S BC-187 TERMINAL, MCNARY'S B-980 L/S AND A/B DISC. MCNARY OPS TO WORK WITH BENTON COUNTY PUD ON MCC'S BEHALF TO PICKUP CLEARANCE ON THEIR BC-187 TERMINAL
24-12866 |  | 11/04/2024 08:00 | 12/10/2024 15:00 | MESA-CONNELL SECTION OF BENTON-SCOOTENEY NO 1 115KV LINE | CONNELL-SCOOTENEY SECTION OF BENTON-SCOOTENEY NO 1 115KV LINE | TCLA | LINE REBUILD | NO SUPPORT FROM ASHE OPERATIONS NEEDED
24-16070 | 16683429 | 11/11/2024 08:00 | 12/06/2024 16:00 | ALVEY-HAYDEN BRIDGE SWITCHING STATION NO 1 115KV LINE | HAYDEN BRIDGE SW STA: PCB 2690 |  |  | EWEB IS INSTALLING NEW RELAY PANELS FOR THEIR HAYDEN BRIDGE SWITCHING STATION PCB 2690. THEY WILL BE ISOLATING THE BREAKER. WE JUST NEED TO LOG THE LINE OUT OF SERVICE.
24-00015 | 9567061 | 11/12/2024 06:00 | 12/06/2024 23:00 | GRAND COULEE: PCB 2492, GRAND COULEE: PCB 2496 |  | GEN, NOH, WOCN | BAY OUTAGE TO SUPPORT RETURN TO SERVICE TESTING OF G24 AFTER TRIENNIAL MAINTENANCE. G24 TRIENNIAL MAINTENANCE IS SCHEDULED FOR 11/20/23 - 3/22/24. (OTS: 6910)
24-15371 | 16586920 | 11/12/2024 08:00 | 12/04/2024 16:00 | ALVEY: B-590 TERMINAL OF ALVEY-CURRIN NO 1 115KV LINE | ALVEY-CURRIN NO 1 115KV LINE, ALVEY: PCB B-590, CURRIN-HAYDEN BRIDGE SWITCHING STATION 115KV LINE | EWEB | EWEB WORK AT CURRIN, REMOVE SHOO-FLY -UNGROUNDED- | PER EWEB,We are removing the shoo-fly around Currin, that created the temporary Alvey-HBSS 115KV line.When this work is finished, we will again have an Alvey-Currin No 1 115KV line and a Currin-HBSS 115KV line.RELAY WORK AT HAYDEN BRIDGE SS AS WELL ON PCB 2690. REMOVING
24-16401 | 16736561 | 11/14/2024 07:00 | 01/07/2025 15:00 | JOHN DAY: 500 KV PCB 4137 INCLUDING MOD 4136 | JOHN DAY: PCB 4137 | NWACI, WOJD, PDCI | REPLACE MOD 4136 | SECTION OF BUS BETWEEN MOD 4136 AND 500 KV EAST BUS TO BE REMOVED UNDER OUTAGE FORM # 24-11936. BUS TO BE TAGGED FOR CLEARANCE HOLDER TO REPLACE MOD 4136
24-15637 |  | 11/14/2024 15:00 | 04/18/2025 16:00 | ALVEY: A-242 M/B AND A/B DISCS |  |  | REMOVE RETIRED PCB A-242. | PCB A-242 WAS PREVIOUSLY THE 230/115KV XFMR BK 3 HIGH SIDE PCB. IT WAS REPLACED BY PCB A-475 DURING ITOA: 24-02802 AND 24-14529 AND IS SCHEDULED TO BE RETIRED/REMOVED AT THE CONCLUSION OF THIS OUTAGE.230KV CONDUCTOR CONNECTING PCB A-242 TO OLD 230/115KV XFMR BK 3 WILL BE REMOVED DURING 230KV SOUTH AUX BUS OUTAGE (ITOA: 24-13839) BETWEEN 10/23/24 AND 10/24/24.ADDITIONAL OUTAGES WILL BE ADDED AT A LATER DATE TO DISCONNECT A-242 M/B AND A/B DISCONNECTS FROM THE POWER SYSTEM.SEE REMARKS, ATTACHMENTS, AND RELATED OUTAGES FOR ADDITIONAL INFORMATION.
24-15723 |  | 11/14/2024 15:00 | 03/13/2025 16:00 | ALVEY: B-584 M/B AND A/B DISCS |  |  | RE-PURPOSE PCB B-584. | PCB B-584 WAS PREVIOUSLY THE 230/115KV XFMR BK 3 LOW SIDE PCB. PCB B-578 BECAME THE NEW 230/115KV XFMR BK 3 LOW SIDE PCB DURING ITOA: 24-02802 AND 24-14529. PCB B-584 WILL BECOME THE NEW TERMINAL PCB FOR THE SPRINGFIELD UTILITY BOARD 115KV FEEDER 1 TO 10TH STREET (ITOA: 25-00323).CONDUCTOR CONNECTING PCB B-584 TO THE OLD 230/115KV XFMR BK 3 WILL BE REMOVED UNDER ITOA 24-11121.SEE REMARKS TABS, RELATED OUTAGES, AND ATTACHMENTS FOR ADDITIONAL INFORMATION.
24-10441 | 16155911 | 12/02/2024 06:00 | 12/13/2024 17:00 | GRIZZLY: PCB 5031 |  | NWACI, WOJD | REPLACE THE PCB 5031 SEL-BFR.
24-00225 | 14278354 | 12/02/2024 06:00 | 12/12/2024 17:00 | JOHN DAY: 4138/4139 TERMINAL OF JOHN DAY PH-JOHN DAY NO 1 500KV LINE | JOHN DAY: 4138/4139 TERMINAL OF JOHN DAY PH-JOHN DAY NO 1 500KV LINE, JOHN DAY PH-JOHN DAY NO 1 500KV LINE | GEN, NWACI, FCRPS, SIG, WOJD | Transformer and Isophase Inspections
24-11113 | 16072887 | 12/02/2024 07:00 | 12/13/2024 16:00 | CUSTER: 4268 BFR | CUSTER: PCB 4268 | BCHT, BCHW, NOEL, SOC, NI | REMOVE BFR AND WIRE, TEST, TRIP CHECK AND IN SERVICE CHECK FOR REPLACEMENT BFR | TIME RESTRICTED REQUEST TO REPLACE ALL SEL BFRS BEFORE 2025 START. OLD SEL BFR UNWIRED AND REMOVED. REPLACEMENT SEL-352 BFR WIRED, SET AND TESTED. TRIP CHECKS AND IN SERVICE CHECKS ON RELATED OUTAGES. WORK MAY EXTEND TO FRIDAY.- PER TOOP, THIS WORK IS WEATHER-DEPENDENT. WORK CAN PROCEED IF TEMPS ARE 34F AND ABOVE IN LOCAL AREA.
24-09965 | 15910548 | 12/02/2024 07:00 | 12/05/2024 15:00 | HANFORD: 500KV NORTH BUS INCLUDING PCB 4107 | HANFORD: PCB 4107, HANFORD: 500KV NORTH BUS | NOH, WOM, WOS | MOD MECHANISM REPLACEMENT | NOT A COMPLETE MOD REPLACEMENTSUB MAINTENANCE WILL REPLACE ALL THREE MOD MECHANISMS ONLYHISTORICALLY MOD HAS CAUSED PHASE DISCORDANCE AND HAS FAILED TO OPEN ALL THREE PHASES WHEN AN OPEN COMMAND WAS SENTMOTOR AND MOTOR CONTACTOR HAVE ALREADY BEEN REPLACED IN C PHASE. THIS DID NOT CORRECT THE ISSUE
24-14503 | 16468743 | 12/02/2024 07:00 | 12/02/2024 16:00 | COVINGTON-MAPLE VALLEY NO 2 230KV LINE, INCLUDING MAPLE VALLEY: PCB A-1114 AND 230KV AUX BUS SECT 1 | MAPLE VALLEY: PCB A-1114 | NOEL, SOC | COMPLETE SERVICES ON A-1114 L/S AND A/B DISCONNECTS
24-13793 |  | 12/02/2024 08:00 | 12/02/2024 12:00 | ALVEY: 115KV MAIN BUS DIFFERENTIAL RELAY |  |  | WIRING WORK TO FACILITATE INSTALLATION OF NEW 115KV BUS DIFFERENTIAL RELAYS AND 115KV BUS SECTIONALIZING PCB. | THIS WORK WILL INVOLVE CONNECTING WIRING FROM THE PCB B-594 BFR TRIP OUTPUT TO THE NEW 115KV MAIN BUS DIFFERENTIAL RELAY SET 2 ONLY.CURRENT 115KV MAIN BUS DIFFERENTIAL RELAYS ARE NON-REDUNDANT AND WILL BE OUT OF SERVICE FOR A SHORT DURATION (LESS THAN 30 MINUTES) TO FACILITATE THIS WORK.THE CURRENT CONNECTION FROM THE PCB B-594 BFR TRIP OUTPUT TO THE CURRENT 115KV MAIN BUS DIFFERENTIAL LOR WILL REMAIN INTACT UNTIL ALL CUTOVERS ARE COMPLETE AND THE NEW 115KV MAIN BUS DIFFERENTIALS ARE READY TO BE PLACED IN-SERVICE AT A LATER DATE.SEE ITOA 24-13792 FOR OUTAGE ON PCB B-594.
24-12405 | 16192409 | 12/02/2024 08:00 | 12/12/2024 15:00 | ASHE: PCB 4898 BFR | ASHE: PCB 4898 | NWACI, FCRPS | REPLACE BFR | REPLACE PCB 4898 SEL-BFR WITH AN SEL-352. THIS IS AN URGENT REQUEST AS SEL-BFR RELAYS HAVE A HIGH FAILURE RATE.
24-12516 | 16201245 | 12/02/2024 08:00 | 12/06/2024 15:00 | JOHN DAY: PCB 4173 SEL BFR AND BREAKER DIFF | JOHN DAY: PCB 4173 | NWACI, WOJD, PDCI | PCB 4173 (112E) SEL BFR RELAY REPLACEMENT & BKR. DIFF PM | INSERVICE READINGS NEED TO BE PERFORMED AT THE CONCLUSION OF MAINTENANCE (12/6/2024). TRIP CHECKS (12/6/2024) FROM SEL 352 WILL BE COMPLETED TO LORs; EAST BUS DIFF SET 2 LOR & PCB 4173 BFR LOR. WHILE PCB 4173 IS ISOLATED, TRIP CHECKS FROM PCB 4176 BFR LOR, EAST BUS DIFF LOR SET 1 & SET 2 WILL BE COMPLETED O.A.T.
24-11311 | 16049601 | 12/02/2024 08:00 | 12/13/2024 15:00 | ALLSTON: PCB 4696 BFR | ALLSTON: PCB 4696 | SOA, NOPE | REPLACE SEL-BFR with SEL-352 | REPLACE SEL-BFR with SEL-352 will need to cutout XFMR#2 LOR and SOUTH BUS LOR multiple times to remove equipment and perform trip checks. Will trip from 500kV DBC LOR. Will need to perform in-service checks at conclusion.WO#599028
24-03963 | 15390294 | 12/02/2024 08:00 | 12/05/2024 15:00 | ECHO LAKE: PCB 5114, BFR |  | BCHT, BCHW, NOEL, SOC, WOCN, NI | ECHO LAKE PCB 5114 BFR MAINTENANCE, IN SERVICE, TRIP CHECKS | Will request PCB 5111 be opened temporarily (15 minutes) to force current through PCB 5114 for in-service checks once PCB 5114 has been restored.
24-10053 | 16374187 | 12/02/2024 08:00 | 12/05/2024 15:00 | MALIN: PCB 4327 INCLUDING THE 500KV REACTOR 1 | MALIN: 500KV REACTOR 1, MALIN: PCB 4327 | COI, NWACI | PCB Diagnostic Service | TOOP - CANNOT TAKE THIS OUTAGE IF REACTOR 2 IS STILL OOS
24-13693 |  | 12/02/2024 08:00 | 12/07/2024 15:00 | SNIPES-ACORD SECTION OF THE GRANDVIEW-RED MOUNTAIN #1 115kV LINE INCLUDING THE CHANDLER TAP | CHANDLER-ACORD SECTION OF GRANDVIEW-RED MOUNTAIN NO 1 115KV LINE, SNIPES-CHANDLER SECTION OF GRANDVIEW-RED MOUNTAIN NO 1 115KV LINE | GEN, TCLA, LOAD | REPLACE SWITCHES B-823 & B-835, TAP SPAN RE-CONDUCTOR AND STRUCTURE RE-BUILD Crew will be changing out switches, associated switch structures and Tap span | TLM HAS CONTACTED CHANDLER PH (USBR) AND VERIFIED THIS TIME FRAME WORKS FOR THEMRecommended Switching:@ Acord break loop with B-2181 @ Snipes Drop roughly 9 miles of line with B-2181 (Full stack of Bottles)@ Chandler Tap (On a dead line) Open and Tag B-2182.
24-16321 | 16718479 | 12/02/2024 08:00 | 12/02/2024 15:00 | ALVEY: PCB 5091 |  |  | Diagnostic service on PCB 5091 and compressor test due to pressure alarms earlier in the year.
24-15019 |  | 12/02/2024 08:00 | 12/03/2024 15:00 | ASHE: 230KV BUS DIFFERENTIAL RELAYS |  |  | ROUTINE RELAY MAINTENANCE, TRIP CHECKS, AND IN-SERVICE CHECKS | ROUTINE RELAY MAINTENANCE, TRIP CHECKS, AND IN-SERVICE CHECKS. TRIP AND IN-SERVICE CHECKS WILL BE ON THE LAST DAY. THERE IS ONLY ONE SET OF BUS DIFF RELAYS AND ONE LOR. TRIP CHECKS WILL INCLUDE TRIPPING THE 230KV BUS DIFF LOR FROM A, B, AND C PHASE BUS DIFF RELAYS. BUS DIFF RELAYS ARE CO-11 OVERCURRENT RELAYS, 1 PER PHASE. DURING TESTING A RELAY WILL BE PRE TESTED AND REPLACE THE RELAY TAKEN OUT OF SERVICE TO BE TESTED SO BUS DIFF PROTECTION WILL REMAIN INTACT DURING RELAY TESTING.
24-14879 |  | 12/02/2024 08:00 | 12/05/2024 15:00 | NORTH BONNEVILLE: PCB A-9 RELAYS | NORTH BONNEVILLE: PCB A-9 | WOCS | Relay Maintenance | Isolate PCB A-9Trip checks and in-service last day of outageTrip checks to PCB A-9 & 230kV East and West Bus "set 1" Differential LORs only, (BFR does not trip to set 2 LORS).
24-14693 |  | 12/02/2024 08:00 | 12/05/2024 16:00 | VALHALLA: PCB B-282 RELAYS | VALHALLA: PCB B-282 |  | PCB B-282 RELAY SETS 1 AND 2 (O.A.T.) WITH BFR, TRIP AND IN-SERVICE CHECKS ON THE LAST DAY. TRIP CHECKS WILL INCLUDE TRIPS FROM THE BUS LOR. WILL ALSO NEED TO PERFORM A BYPASS (COLUMBIA-VALHALLA #1 / PCB B-276) IN ORDER TO COMPLETE IN-SERVICE CHECKS (SEE ITOA 24-14694 FOR TRIP CHECK AND BYPASS INFO) | PCB B-282 RELAY SETS 1 AND 2 (O.A.T.) WITH BFR, TRIP AND IN-SERVICE CHECKS ON THE LAST DAY. TRIP CHECKS WILL INCLUDE TRIPS FROM THE BUS LOR. WILL ALSO NEED TO PERFORM A BYPASS (COLUMBIA-VALHALLA #1 / PCB B-276) IN ORDER TO COMPLETE IN-SERVICE CHECKS (SEE ITOA 24-14694 FOR TRIP CHECK AND BYPASS INFO)
24-13069 |  | 12/02/2024 08:00 | 12/05/2024 18:00 | CANAL (SCL)-VIEWLAND 115KV LINE |  | NOEL, SOC
24-02786 | 15038975 | 12/02/2024 08:00 | 12/07/2024 16:00 | SMITHSON-EAST ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE | SMITHSON-EAST ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE | TCLA | #1482026 REMOVE OLD FIBER FOR THE SCHULTZ-FRANKLIN SECTION OF THE ROSS-SCHULTZ FIBER PROJECT.
24-07351 | 15571754 | 12/02/2024 08:00 | 12/05/2024 15:00 | TAFT: PCB 4028 |  | MT-NW, NOH, WOH | DIAGNOSTIC SERVICE
24-07677 | 15628864 | 12/02/2024 08:00 | 12/03/2024 15:30 | BIG EDDY: 500KV WEST BUS INCLUDING PCBS 4205, 4866, 4212, BIG EDDY-CELILO 1 500KV LINE AND CELILO: PCB 4741 | BIG EDDY: 500KV WEST BUS, BIG EDDY: PCB 4205, BIG EDDY: PCB 4866, BIG EDDY: PCB 4212, CELILO: PCB 4741, BIG EDDY-CELILO NO 1 500KV LINE | PDCI, WOCS, WOJD, BGEDY, GEN, NWACI, SIG | COMPLETE SERVICE ON MODS 4206, 4214, 4865 AND 4213 | SCHEDULED TO COINCIDE WITH CELILO SIR
24-00803 | 15233546 | 12/02/2024 08:30 | 12/05/2024 15:00 | SLATT: 230KV CAP GROUP 3 SECT 1 RELAY SETS 1, 2 AND PCB A-1799 BFR | SLATT: PCB A-1799, SLATT: 230KV CAP GROUP 3 SECTION 1, SLATT: SLATT: 230KV CAP GROUP 3 SECTION 1 RELAYS SET 1, SLATT: SLATT: 230KV CAP GROUP 3 SECTION 1 RELAYS SET 2 | COI, NWACI, PDCI, WOJD | ROUTINE CAP GROUP AND BFR RELAY MAINTENANCE | 230KV CAP GROUP 3 SECT 1 INLCUDING PCB A-1799 TO BE ISOLATED FOR DURATION OF MAINTENANCE.TRIP CHECKS TO PCB A-1799, 230KV EAST BUS DIFF LOR SET 1 AND 2 ONE AT A TIME. IN SERVICE CHECKS AT CONCLUSION OF MAINTENANCE. WILL REQUIRE 230KV CAP GROUP 3 SECT 1 TO BE INSERTED FOR APPROXIMATELY 15-30 MIN, IF SYSTEM CONDITIONS ALLOW.
24-15237 |  | 12/02/2024 10:30 | 12/06/2024 15:00 | CGS BACKUP BANK-451B SECTION OF BENTON-WHITE BLUFFS NO 2 115KV LINE | DOE 451B: US DOE RICHLAND 115KV FEEDER 2 |  | PRIORITY POLE REPLACEMENTS AT STRUCTURES 3/6, 3/8, AND 4/3 | 115KV LINE WILL REMAIN IN SERVICE FROM BENTON TO CGS TAP AND INCLUDING THE TAP, CGS TRB WILL BE RADIALLY FED FROM BENTON.451B SUB WILL BE RADIALLY FED FROM WHITE BLUFFSWILL REQUIRE HEW 451B 13.8KV FEEDER 2 LOAD BE TRANSFERRED TO FEEDER 1
24-06653 | 15974373 | 12/03/2024 08:00 | 12/03/2024 14:30 | PEARL: PCB A-1167 |  |  | ROUTINE SERVICE | 230KV BUS TIE POSITIONNO OTHER WORK HAPPENING THAT NEEDS THE BUS TIE ON 12/3/2024
24-15096 |  | 12/03/2024 08:00 | 12/04/2024 17:00 | REDMOND: 230KV WEST MAIN BUS, INCLUDING CENTER MAIN BUS, PCB'S A-262, A-252, A-254, A-256, A-258, AND A-259 | REDMOND: 230KV CENTER MAIN BUS, REDMOND: PCB A-262, REDMOND: PCB A-252, REDMOND: PCB A-254, REDMOND: PCB A-256, REDMOND: PCB A-258, REDMOND: PCB A-259, REDMOND: PCB A-260, REDMOND: 230/115KV TRANSFORMER 5, REDMOND: 230/69KV TRANSFORMER 1, REDMOND: 230/69KV TRANSFORMER 2, REDMOND: 69KV MAIN BUS, REDMOND: 69KV AUX BUS, REDMOND: 69KV PCB L-212, REDMOND: 69KV PCB L-214, REDMOND: 69KV PCB L-216, REDMOND: 69KV PCB L-218, REDMOND: 69KV GROUNDING TRANSFORMER M1, REDMOND: 69KV GROUNDING TRANSFORMER K1, REDMOND: CENTRAL ELEC COOP 69KV FEEDER 1, REDMOND: PACIFICORP (PACW) 69KV FEEDER 1 | COR, NWACI, COI, PDCI, GRZN | DISCONNECT COMPLETE SERVICES | DISCONNECT COMPLETE SERVICES ON THE FOLLOWING MAIN BUS DISCONNECTS: A-262, A-252, A-254, A-256, A-258, A-257 AND A-259 (WEST SIDE).PGE-ROUND BUTTE 230KV LINE TO BE LONG-LINED WITH PACW-PILOT BUTTE 230KV LINE OVER 230KV WEST AUX BUS. REQUEST PGE AND PACW TECHNICAL RELAYING SUPPORT FOR LONG LINE CONFIGURATION.FORCES OUT 230/115/13.8KV TRANSFORMER 5. BANK3 TO SUPPORT 115KV LOADS AND 13.8KV STATION SERVICE.FORCES OUT 230/69KV BANKS 1 AND 2, PACW 69KV FEEDER 1 AND CEC 69KV FEEDER 1. REQUEST PACW REDMOND SUB 69KV TERMINAL (???) TO STAY NORMAL (UNLOADED). CEC TO CLOSE THEIR DESCHUTES JUNCTION SUB DISCONNECT S-338 FOR PACW TO SUPORT CEC'S 69KV LOADS. REDMOND OPS VERIFIED CEC SUPPORT FOR THIS CONFIGURATION.
24-15823 | 16689220 | 12/03/2024 10:00 | 12/03/2024 10:15 | GRAND COULEE: PCB 2292, GRAND COULEE: PCB 2296 |  | GEN, NOH, WOCN | Bay outage to support removing G-22 from service for commutator stoning.
24-15824 | 16689226 | 12/03/2024 14:15 | 12/03/2024 14:30 | GRAND COULEE: PCB 2292, GRAND COULEE: PCB 2296 |  | GEN, NOH, WOCN | Bay outage to support returning G-22 to service after commutator stoning.
24-14505 | 16468837 | 12/04/2024 07:00 | 12/04/2024 16:00 | KLAHANIE-MAPLE VALLEY SECTION OF SAMMAMISH-MAPLE VALLEY NO 1 230KV LINE, INCLUDING MAPLE VALLEY: PCB A-1136 AND 230KV AUX BUS SECT 3 | MAPLE VALLEY: PCB A-1136 | NOEL, SOC, SIG | COMPLETE SERVICES ON A-1136 L/S AND A/B DISCONNECTS | 31AUG24: PSE CONFIRMED THEY CAN SUPPORT. RPT
24-07678 | 15628900 | 12/04/2024 08:00 | 12/05/2024 15:30 | BIG EDDY: 500KV EAST BUS INCLUDING PCB'S 4200, 4872, 4860, BIG EDDY-CELILO 2 500KV LINE AND CELILO: PCB 4740 | BIG EDDY: 500KV EAST BUS, BIG EDDY: PCB 4200, BIG EDDY: PCB 4872, BIG EDDY: PCB 4860, CELILO: PCB 4740, BIG EDDY-CELILO NO 2 500KV LINE | PDCI, WOCS, WOJD, BGEDY, NWACI, SIG | COMPLETE SERVICE ON MODS 4207, 4159, 4873 AND 4208 | SCHEDULED TO COINCIDE WITH CELILO SIR
24-15743 |  | 12/04/2024 09:00 | 12/04/2024 15:00 | PSE - HORSE RANCH PCB 7023, 7411 OR 7412 | HORSE RANCH TAP TO MONROE-SNOHOMISH NO 1&2 230KV LINE | BCHT, BCHW, NOEL, SOC, SIG | PSE WORK-PCB OPEN ONE AT A TIME TO VERIFY COMMUNICATION, CONTROL AND METERING
24-14506 | 16468847 | 12/05/2024 07:00 | 12/05/2024 16:00 | MAPLE VALLEY-TALBOT NO 1 230KV LINE, INCLUDING MAPLE VALLEY: PCB A-1120 AND 230KV A/B SECT 1 | MAPLE VALLEY: PCB A-1120 | NOEL, SOC | COMPLETE SERVICES ON A-1120 L/S AND A/B DISCONNECTS | 31AUG24: PSE CONFIRMED THEY CAN SUPPORT. RPT
24-14694 |  | 12/05/2024 08:00 | 12/05/2024 15:00 | VALHALLA: PCB B-282 RELAYS | VALHALLA: PCB B-282, VALHALLA: PCB B-276 |  | PCB B-282 RELAY SETS 1 AND 2 WITH BFR, TRIP AND IN-SERVICE CHECKS ON THE LAST DAY. TRIP CHECKS WILL INCLUDE TRIPS FROM THE BUS LOR. WILL ALSO NEED TO PERFORM A BYPASS (COLUMBIA-VALHALLA #1 / PCB B-276) IN ORDER TO COMPLETE IN-SERVICE CHECKS | PCB B-282 RELAY SETS 1 AND 2 WITH BFR AND TRIP CHECKS ON THE LAST DAY. TRIP CHECKS WILL INCLUDE TRIPS FROM THE BUS LOR. WILL ALSO NEED TO PERFORM A BYPASS (COLUMBIA-VALHALLA #1 / PCB B-276) IN ORDER TO COMPLETE IN-SERVICE CHECKS
24-05621 | 15753734 | 12/05/2024 08:00 | 12/05/2024 14:30 | KEELER: PCB 4763, INCLUDING 500KV CAP GROUP 3 | KEELER: 500KV CAP GROUP 3 | SOA, NOPE, WOCS | ROUTINE SERVICE | PCB 4763 SOURCES 500KV CAP GROUP #3SWITCHING NOTES:PLACE 500KV CAP GRP #3 AVC SWITCH IN MANUALTAKE LOCAL CONTROL OF RAS AC A AND AC B REACTIVE CONTROLLERSCUT OUT MAINT SWITCHES ON RAS AC A AND AC B REACTIVE CONTROLLERS
24-01512 | 14885515 | 12/05/2024 08:00 | 12/05/2024 15:00 | MARION: PCB 4012 | MARION: PCB 4012, MARION: 500KV REACTOR 1 | NWACI | ROUTINE RELAY MAINTENANCE 4012 BFR & DIFFERENTIAL RELAYS WITH PCB ISOLATED, FOLLOWED BY TRIP/IN-SERVICE CHECKS. | FORCES OUT 500KV REACTOR 1
24-10995 | 15996878 | 12/07/2024 07:00 | 12/07/2024 16:00 | COVINGTON: 500/230KV TRANSFORMER 4 INCLUDING 34.5KV PCBS L-1901 AND L-1902 | COVINGTON: 500/230KV TRANSFORMER 4, COVINGTON: PCB L-1901, COVINGTON: PCB L-1902, RAVER-COVINGTON NO 1 500KV LINE | NOEL, RP, SIG, SOC, NI, WOCN, IROL | CUT OVER BANK COOLING CIRCUITS TO NEW ATS | IF THE CURRENTLY INSTALLED 480V ATS #1 WERE TO FAIL, BANK 4 COOLING CIRCUITS WOULD BE DE-ENERGIZED. THIS WORK WILL CUT THESE CIRCUITS OVER TO A NEWLY INSTALLED ATS WHICH WILL PROVIDE A BACKUP SOURCE TO KEEP THE COOLING CIRCUITS ENERGIZED. THIS IS BEING INSTALLED AS PART OF THE EG REPLACEMENT PROJECT.***PRIOR TO DE-ENERGIZATION OF THIS BANK, OPERATOR MUST CLOSE PCB L-1907 AND OPEN PCB L-1902 TO KEEP POWER ON IN THE COVINGTON DISTRICT BUILDINGS***
24-16375 |  | 12/09/2024 05:00 | 12/20/2024 19:00 | LADWP - VICTORVILLE-CENTRURY 2 287KV LINE |  | PDCI | LADWP WORK
24-16459 | 16737310 | 12/16/2024 07:30 | 12/16/2024 10:30 | MALIN: 500KV REACTOR 2 INCLUDING PCB 4037 | MALIN: PCB 4037, MALIN: 500KV REACTOR 2 | NWACI, COI | B PHASE OIL SAMPLE | WEEKLY 500 KV REACTOR 2 B PHASE OIL SAMPLES TO BE TAKEN WHILE EQUIPMENT IS ISOLATED DUE TO INSTALLED REACTOR BEING SUSPECT EQUIPMENT DUE TO PAST GASSING ISSUES UNTIL DEEMED OTHERWISE.SUDDEN PRESSURE RELAY CUT OUT FOR OIL SAMPLES
24-12517 | 16209745 | 12/09/2024 08:00 | 12/13/2024 16:00 | JOHN DAY: PCB 4176 SEL BFR AND BREAKER DIFF RELAY | JOHN DAY: PCB 4176 | NWACI, WOJD, PDCI | PCB 4176 (115E) SEL BFR RELAY REPLACEMENT & BKR. DIFF PM | INSERVICE READINGS NEED TO BE PERFORMED AT THE CONCLUSION OF MAINTENANCE (12/13/2024). TRIP CHECKS (12/13/2024) FROM SEL 352 WILL BE COMPLETED TO PCB 4176 BFR LOR. WHILE PCB 4176 IS ISOLATED, TRIP CHECKS FROM PCB 4173 BFR LOR, AND PCB LOR 4179 WILL BE COMPLETED O.A.T.
24-07616 |  | 12/09/2024 08:00 | 12/12/2024 15:00 | REDMOND: 230KV CAP GROUP 1 RELAY SET 1 AND 2, AND A-264 BFR | REDMOND: 230KV CAP GROUP 1, REDMOND: PCB A-264 | COR, NWACI
24-09001 |  | 12/09/2024 08:00 | 12/19/2024 15:00 | ADDY: DFR |  |  | REPLACE DFR BATTERY AND CALIBRATE ALL USED CHANNELS | SUBMITTING THIS AS A COURTESY TO MCC, AS CURRENTS AND POTENTIALS THAT GO TO RELAYS CAN POSSIBLY BE AFFECTED, THOUGH NO ISSUES ARE ANTICIPATED
24-13505 |  | 12/09/2024 08:00 | 12/13/2024 17:00 | MCNARY-FRANKLIN NO 2 230KV LINE | FRANKLIN: PCB B-622, FRANKLIN: 230/115KV TRANSFORMER 4, MCNARY: PCB A-437 | WOM, TCLA | TOWER TC-9 REINFORCEMENT | CLEARANCE LIMITS:MCNARY- A-437 L/S AND A/B DISCFRANKLIN- A-884 LSD
24-15480 |  | 12/09/2024 08:00 | 12/13/2024 17:00 | MCNARY-B-1345 SECTION OF THE MCNARY-BADGER CANYON NO. 1 115KV LINE INCLUDING PLYMOUTH TAP AND BC-165 DISC | PLYMOUTH TAP TO MCNARY-BADGER CANYON NO 1 115KV LINE, MCNARY: PCB B-980, MCNARY-B-1345 SECTION OF MCNARY-BADGER CANYON NO 1 115KV LINE | TCLA, GEN, WOM, LOAD | PROXIMITY WORK FOR TC 9 REINFORCEMENT | GROUND SWITCH 7472 REQUESTED CLOSED CLEARANCE LIMITS:B-1345 LSDB-980 L/S AND A/B DISCBC-187 FROM BENTON COUNTY PUDCONTACT INFO:FORSMANN 971-678-6878
24-02787 | 15039615 | 12/09/2024 08:00 | 12/09/2024 16:00 | SMITHSON-ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE, INCLUDING EAST ELLENSBURG TAP TO B-665 DISCONNECT | SMITHSON-ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE, INCLUDING EAST ELLENSBURG TAP TO B-665 DISCONNECT, SMITHSON-EAST ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE, EAST ELLENSBURG TAP TO COLUMBIA-ELLENSBURG NO 1 115KV LINE, EAST ELLENSBURG-ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE, EAST ELLENSBURG: CITY OF ELLENSBRG 115KV FEEDER 1, HELENA AVENUE: CITY OF ELLENSBRG 115KV FEEDER 1 | TCLA | #1482028 REMOVE OLD FIBER FOR THE SCHULTZ-FRANKLIN SECTION OF THE ROSS-SCHULTZ FIBER PROJECT.
24-05622 | 15688053 | 12/09/2024 08:00 | 12/12/2024 17:00 | KEELER: PCB A-873 INCLUDING THE 230KV REACTIVE GROUP 2 REACTOR 1 | KEELER: 230KV REACTIVE GROUP 2 REACTOR 1, KEELER: PCB A-873 | SOA, NOPE | DIAGNOSTIC SERVICE | THE SVC WILL BE AVAILABLE FOR REACTIVE SUPPORT DURING THIS OUTAGE
24-07684 | 15628936 | 12/09/2024 08:00 | 12/09/2024 15:30 | JOHN DAY-BIG EDDY 2 500KV LINE INCLUDING BIG EDDY: PCB'S 4200 AND 4202 | JOHN DAY-BIG EDDY NO 2 500KV LINE, BIG EDDY: PCB 4200, BIG EDDY: PCB 4202, JOHN DAY: PCB 4176, JOHN DAY: PCB 4179 | NWACI, WOJD, BGEDY, PDCI, WOCS | COMPLETE SERVICE ON MODS 4201 AND 4160 | SCHEDULED TO COINCIDE WITH CELILO SIR
24-07038 | 15490659 | 12/09/2024 08:00 | 12/09/2024 17:00 | ROCK CREEK: PCB 5294 |  | RKCR, NOH | ROUTINE SERVICE | BANK 1 / WAUTOMA
24-13175 | 16556921 | 12/10/2024 07:00 | 12/10/2024 15:00 | SHELTON: PCB A-941 |  | RP | BFR Maintenance and Trip Checks. Trip checks only to A-941 through associated LOR's. LOR's will be cut-out for less than 30 minutes.
24-07685 | 15628992 | 12/10/2024 08:00 | 12/10/2024 15:30 | BIG EDDY-KNIGHT 1 500KV LINE INCLUDING BIG EDDY: PCB'S 4209 AND 4860 | BIG EDDY-KNIGHT NO 1 500KV LINE, BIG EDDY: PCB 4209, BIG EDDY: PCB 4860, KNIGHT: PCB 5471, KNIGHT: PCB 5474 | PDCI, SIG, WOCS, WOJD, BGEDY, NWACI, GEN, WOCN, NOH | COMPLETE SERVICE ON MODS 4861 AND 4862 | SCHEDULED TO COINCIDE WITH CELILO SIR
24-02788 | 15045096 | 12/10/2024 08:00 | 12/14/2024 16:00 | EAST ELLENSBURG-ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE | EAST ELLENSBURG-ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE | TCLA | #1482030 REMOVE OLD FIBER FOR THE SCHULTZ-FRANKLIN SECTION OF THE ROSS-SCHULTZ FIBER PROJECT.
24-14737 | 16556934 | 12/10/2024 14:30 | 12/10/2024 15:00 | SHELTON: PCB A-83 |  | RP | OPEN FOR INSERVICE ON PCB A-941 BFR
24-13177 | 16592791 | 12/11/2024 07:00 | 12/11/2024 15:00 | SHELTON: PCB A-976 |  | RP | BFR Maintenance and Trip Checks. Trip checks only to A-976 through associated LOR's. LOR's will be cut-out for less than 30 minutes.
24-15450 |  | 12/11/2024 07:00 | 12/11/2024 19:00 | OLYMPIA: 230KV WEST AUX BUS | OLYMPIA: 230KV WEST AUX BUS, OLYMPIA: PCB A-216 | NOEL, RP, SOC, WOCN | WELD RISER FROM 230KV WEST A/B TO A-218 A/B DISCONNECT | WILL TEST ENERGIZE A-218 WITH 230KV BUS TIE PCB A-216
24-14413 | 16455973 | 12/11/2024 07:00 | 12/21/2024 15:00 | ST JOHNS-DUTCH CANYON SECTION OF ST JOHNS-ST HELENS NO 1 115KV LINE |  | LOAD, SOA, NOPE | THEIR PROXIMITY WORK STRINGING NEW CONDUCTOR
24-14412 | 16455945 | 12/11/2024 08:00 | 12/21/2024 16:00 | ST JOHNS-KEELER NO 2 115KV LINE |  | LOAD, SOA, NOPE | PGE PROXIMITY STRINING NEW CONDUCTOR
24-08703 | 16225691 | 12/11/2024 08:00 | 12/11/2024 16:00 | WHITE BLUFFS: PCB B-1362 INCLUDING 115KV CAP GRP NO. 1 | WHITE BLUFFS: PCB B-1362, WHITE BLUFFS: 115KV CAP GROUP 1 | LOAD | ROUTINE SERVICE ON PCB B-1362 AND 115KV CAP GRP NO.1 | ROUTINE SERVICE ON PCB B-1362 AND 115KV CAP GRP NO.1
24-07690 | 15629049 | 12/11/2024 08:00 | 12/11/2024 17:30 | BIG EDDY: 500/230KV TRANSFORMER BANK 2 INCLUDING 500/230KV TIE NO 1 500KV LINE AND PCB'S 4866 AND 4870 | BIG EDDY: 500/230KV TRANSFORMER 2, BIG EDDY 500/230KV TIE NO 1 500KV LINE, BIG EDDY: PCB 4866, BIG EDDY: PCB 4870, BIG EDDY: PCB A-848, BIG EDDY: 34.5KV PCB L-1710, BIG EDDY: 34.5/13.2KV TRANSFORMER 6, BIG EDDY: 13.2KV PCB L-1470, BIG EDDY: 13.2KV PCB L-1474 | GEN, PDCI, SIG, FCRPS, WOJD, BGEDY, NWACI, SOA, NOPE | COMPLETE SERVICE ON MODS 4867 AND 4868 | SCHEDULED TO COINCIDE WITH CELILO SIRCELILO TO TRANSFER LOAD OFF OF CELILO 13.2KV FDR NO. 2 AND OPEN BIGE PCB L-1474.BIG EDDY TO DROP TRANSFER BANK 6 STATION SERVICE TO BANK 4 PRIOR TO SWITCHING. PERFORMED WITH LOW VOLTAGE ACBS. BANK 4 WILL SUPPLY ALL BIGE STATION SERVICE.
24-08293 |  | 12/11/2024 08:00 | 12/11/2024 17:30 | BIG EDDY: A-848 AUX BUS DISC, BIG EDDY: A-848 TRANSFORMER SIDE DISC |  |  | COMPLETE SERVICE ON MODS 4867 AND 4868 | SCHEDULED TO COINCIDE WITH CELILO SIRCELILO TO TRANSFER LOAD OFF OF CELILO 13.2KV FDR NO. 2 AND OPEN BIGE PCB L-1474.BIG EDDY TO DROP TRANSFER BANK 6 STATION SERVICE TO BANK 4 PRIOR TO SWITCHING. PERFORMED WITH LOW VOLTAGE ACBS. BANK 4 WILL SUPPLY ALL BIGE STATION SERVICE.
24-14736 | 16592802 | 12/11/2024 15:01 | 12/11/2024 15:30 | SHELTON: PCB A-79 |  | RP | OPEN FOR IN-SERVICE ON PCB A-976 BFR
24-15765 |  | 12/12/2024 07:00 | 12/12/2024 19:00 | OLYMPIA: 230KV WEST MAIN BUS | OLYMPIA: PCB A-222, OLYMPIA: PCB A-220, OLYMPIA: PCB A-218, OLYMPIA: PCB A-216, OLYMPIA-SATSOP NO 2 230KV LINE, CHEHALIS-OLYMPIA NO 1 230KV LINE, OLYMPIA: 230/115KV TRANSFORMER 1, OLYMPIA-SHELTON NO 4 230KV LINE, OLYMPIA: 230KV CAP GROUP 2 SECTION 1, OLYMPIA: 230KV CAP GROUP 2 SECTION 2 | RP, LOAD, NOEL, SI, SOC, WOCN, SOA, NOPE | WELD IN A-218 M/B RISER BETWEEN THE 230 WEST M/B AND A-218 M/B DISC AND RESTORE 230/115KV XFMR BK #1 TO NORMAL SERVICE | STATION SERVICE IS CURRENTLY BEING FED FROM 230/115KV XFMR BANK 2230/15KV XFMR BK #2 WILL REMAIN IN SERVICE230KV OLYMPIA-SHELTON #4 LINE WILL BE FORCED OUT DUE TO M/B PT BEING DE-ENERGIZED230KV CAP GROUP 2, SECTIONS 1 AND 2 WILL BE FORCED OUT DUE TO M/B PT BEING DE-ENERGIZED OLYMPIA-SATSOP #2 WILL BE FORCED OUT DUE TO M/B PT BEING DE-ENERGIZED - PER TOOP, THIS WORK IS WEATHER-DEPENDENT. WORK CAN PROCEED IF TEMPS ARE 34F AND ABOVE IN LOCAL AREA.
24-15023 | 16592854 | 12/12/2024 08:00 | 12/12/2024 11:00 | WINE COUNTRY: PCB A-1741 |  | WOJD, NOH | TRIP CHECKS PCB TO BE ISOLATED FOR TRIP CHECKS SEE RELATED ITOA 24-15022
24-15024 | 16592895 | 12/12/2024 12:00 | 12/12/2024 15:00 | WINE COUNTRY: PCB A-1747 |  | WOJD, NOH | TRIP CHECKS ISOLATE PCB FOR TRIP CHECKS SEE RELATED ITOA 24-15022
24-11117 | 16072960 | 12/13/2024 16:00 | 12/13/2024 16:30 | CUSTER: PCB 4272 |  | BCHT, BCHW, NOEL, SOC, NI | IN SERVICE CHECKS | RELATED OUTAGE 24-11113. PCB 4272 OPENED TO FORCE CUST-MONE 1 LINE LOAD THROUGH PCB 4268 FOR IN SERVICE CHECKS.- PER TOOP, THIS WORK IS WEATHER-DEPENDENT. WORK CAN PROCEED IF TEMPS ARE 34F AND ABOVE IN LOCAL AREA.
24-10445 | 16187733 | 12/16/2024 06:00 | 12/31/2024 17:00 | GRIZZLY: PCB 5028 |  | NWACI, WOJD | REPLACE THE PCB 5028 SEL-BFR
24-00924 |  | 12/16/2024 07:00 | 01/17/2025 16:00 | MCNARY: 115KV AUX BUS INCLUDING B-979 A/B DISC | MCNARY: PCB B-988, MCNARY: 115KV AUX BUS |  | INSTALL NEW MCNARY-BERRIAN #1 115KV TRANSMISSION LINE FROM 0/1-TC 9 | CLEARANCE LIMITS:B-978, B-980, B-986, B-988, B-990, B-987, B-994, B-995, B-997 A/B AND B-979 L/S DISCONNECTS
24-16459 | 16737355 | 12/16/2024 07:30 | 12/16/2024 10:30 | MALIN: 500KV REACTOR 2 INCLUDING PCB 4037 | MALIN: PCB 4037, MALIN: 500KV REACTOR 2 | NWACI, COI | B PHASE OIL SAMPLE | WEEKLY 500 KV REACTOR 2 B PHASE OIL SAMPLES TO BE TAKEN WHILE EQUIPMENT IS ISOLATED DUE TO INSTALLED REACTOR BEING SUSPECT EQUIPMENT DUE TO PAST GASSING ISSUES UNTIL DEEMED OTHERWISE.SUDDEN PRESSURE RELAY CUT OUT FOR OIL SAMPLES
24-12406 | 16209471 | 12/16/2024 08:00 | 12/31/2024 15:00 | ASHE: PCB 4937 BFR | ASHE: PCB 4937 | NOH, NWACI, FCRPS | REPLACE BFR | REPLACE PCB 4937 SEL-BFR WITH AN SEL-352. THIS IS AN URGENT REQUEST AS SEL-BFR RELAYS HAVE A HIGH FAILURE RATE.
24-12518 | 16209779 | 12/16/2024 08:00 | 12/20/2024 16:00 | JOHN DAY: PCB 4179 SEL BFR AND BREAKER DIFF RELAY | JOHN DAY: PCB 4179 | NWACI, WOJD, PDCI | PCB 4179 (118E) SEL BFR RELAY REPLACEMENT & BKR. DIFF PM | INSERVICE READINGS NEED TO BE PERFORMED AT THE CONCLUSION OF MAINTENANCE (12/20/2024). TRIP CHECKS (12/20/2024) FROM SEL 352 WILL BE COMPLETED TO LORs; WEST BUS DIFF SET 2 LOR & PCB 4179 BFR LOR. WHILE PCB 4179 IS ISOLATED, TRIP CHECKS FROM PCB 4176 BFR LOR, WEST BUS DIFF LOR SET 1 & SET 2 WILL BE COMPLETED O.A.T.
24-10663 | 16187478 | 12/16/2024 08:00 | 12/19/2024 15:00 | SLATT: BUCKLEY 1 500KV LINE SERIES CAP GROUP 1 INCLUDING PCB 5012 | SLATT: BUCKLEY 1 500KV LINE SERIES CAP GROUP 1 | WOJD, WOM, WOS, NWACI | ROUTINE INSPECTION OF 500KV SERIES CAP GROUP BANK | SERIES CAPS WILL BE UNAVAILABLE WITH SLATT-BUCKLEY LINE REMAINING INTACT.WORK PERMIT FOR FIRMWARE UPDATE BEING PERFORMED DURING OUTAGE, SEE 24-10698GROUND SWITCHES 7948 AND 7949 WILL BE CLOSED
24-13760 | 16375205 | 12/16/2024 08:00 | 12/17/2024 15:00 | CAPTAIN JACK: PCB 4924 |  | NWACI, COI | PCB Routine
24-16097 | 16687539 | 12/16/2024 08:00 | 12/16/2024 15:00 | ABERDEEN TAP-COSMOPOLIS SECTION OF SATSOP PARK-COSMOPOLIS NO 1 115KV LINE | SATSOP PARK-COSMOPOLIS NO 1 115KV LINE | LOAD, SOA, NOPE, RP | INSTALL HOLD DOWN WEIGHTS AT 12/6 TO FINISH LINE UPGRADE WORK
24-14814 |  | 12/16/2024 08:00 | 12/16/2024 17:00 | THE DALLES-DISCOVERY #1 115KV LINE INCLUDING THE DALLES PCB B-1104 AND 115KV AUXILIARY BUS | HOOD RIVER: PCB B-1680, CASCADE LOCKS-HOOD RIVER SECTION OF BONNEVILLE PH 1-HOOD RIVER NO 1 115KV LINE, FOSSIL: 69KV PCB L-1376, FOSSIL-MUDDY RANCH SECTION OF FOSSIL-MAUPIN 69KV LINE, DISCOVERY: PCB B-2012, THE DALLES: PCB B-1104, THE DALLES: 115KV AUX BUS, THE DALLES-DISCOVERY NO 1 115KV LINE | GEN, BGEDY | COMPLETE SERVICE ON B-1104 L/S MOD AND B-1104 A/B DISCONNECTS | THE 115KV A/B IS NORMALLY ENERGIZED FROM THE HOOD RIVER POSITION. NO BUSTIE BREAKER AT THE DALLES.NORTHERN WASCO PUD GEOFFREY LACEFIELD CONFIRMED THEY CAN SUPPORT THIS OUTAGE ON 8-27-2024 VIA E-MAIL....WJGDISTRICT OPERATOR TO NOTIFY WEC 541-296-2740, CBEC 541-676-9146 AND CPC 541-934-2311 TO VERIFY THAT THE 69KV LOOP IS NORMAL PRIOR TO SWITCHING IF FOSSIL PCB L-1376 WILL BE OPEN.NOTIFY NWPUD THE DISCOVERY SUB WILL BE SINGLE SOURCED FROM CHENOWETH.THE AGREEMENT BETWEEN BPA AND NWPUD SAYS NWPUD WILL OPERATE THE B-2010, B-2011 AND B-2013 DISCONNECTS, BUT FOR BPA WORK WE WILL CHECK OPEN AND TAG THE APPLICABLE DISCONNECT'S ONCE NWPUD HAS OPENED IT. THE DALLES DATS# 4147DSO 327 CONSIDERATIONSc. The Dalles-Discovery #1 115kV line 1) For planned outages: disarm or verify disarmed the “DALLES AREA GEN DROP ARMED” point before switching. 2) For planned outages: use Table 1 Level 4 value to determine Table 2 generation advisories. 3) Open Fossil PCB L1376 breaker for the duration of the outage (Reference NOTE 6). 4) Open Hood River PCB B1680 breaker for the duration of the outage (Reference NOTE 7). a. Verify sufficient voltage control options are available and generation restrictions issued if needed per DSO352, Attachment 1, Bonneville PH 1-Hood River #1 115kV line outage condition.
24-15491 |  | 12/16/2024 08:00 | 01/17/2025 15:00 | MCNARY-B-1345 SECTION OF THE MCNARY-BADGER CANYON NO. 1 115KV LINE INCLUDING PLYMOUTH TAP AND BC-165 DISC | PLYMOUTH TAP TO MCNARY-BADGER CANYON NO 1 115KV LINE, MCNARY: PCB B-980, MCNARY-B-1345 SECTION OF MCNARY-BADGER CANYON NO 1 115KV LINE | TCLA, GEN, WOM, LOAD | PROXIMITY WORK TO INSTALL NEW MCNARY-BERRIAN #1 115KV TRANSMISSION LINE FROM 0/1-TC 9 | GROUND SWITCH 7472 REQUESTED CLOSED CLEARANCE LIMITS:B-1345 LSDB-980 L/S AND A/B DISCBC-187 FROM BENTON COUNTY PUDCONTACT INFO:FORSMANN 971-678-6878
24-02789 | 15045174 | 12/16/2024 08:00 | 12/16/2024 16:00 | JENKINS-EAST ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE INCLUDING SMITHSON TAP | JENKINS-EAST ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE INCLUDING SMITHSON TAP, JENKINS-SMITHSON SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE, SMITHSON-EAST ELLENSBURG SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE, SMITHSON TAP TO COLUMBIA-ELLENSBURG NO 1 115KV LINE | TCLA | #1482036 REMOVE OLD FIBER FOR THE SCHULTZ-FRANKLIN SECTION OF THE ROSS-SCHULTZ FIBER PROJECT.
24-02185 | 15391805 | 12/16/2024 08:00 | 12/19/2024 15:00 | KEELER: 230KV REACTIVE GROUP 2 CAP SECTION 2 INCLUDING LBD A-857 | KEELER: 230KV REACTIVE GROUP 2 CAP SECTION 2, KEELER: LBD A-857 | SOA, WOCS, NOPE | LBD COMPLETE AND CAP INSPECTION | SVC WILL BE AVAILABLE FOR REACTIVE SUPPORTCAP SECTION 3 WILL BE AVAILABLE IF NEEDED:PLACE PCB A-859 ON L/C WITH AVC SWITCH FOR CAP SECT 3 IN MANUALCALL WORKERS INTO THE CLEAR BEFORE OPERATING (THEY WILL BE WORKING IN THE ADJACENT CAP SECTION)
24-07352 | 15629162 | 12/16/2024 08:00 | 12/19/2024 15:00 | TAFT: 500KV REACTOR 1, INCLUDING PCB 4145 | TAFT: PCB 4145, TAFT: 500KV REACTOR 1 | MT-NW, WOH | DIAGNOSTIC SERVICE
24-12499 | 16235515 | 12/17/2024 08:00 | 12/17/2024 16:00 | JOHN DAY-MARION NO 1 500KV LINE | JOHN DAY-MARION LINE RELAYS | NWACI, SIG, WOCS, WOJD, PDCI | END - TO - END COMMUNICATION CHECKS ON THE JOHN DAY - MARION NO 1 500 KV LINE | SPC GUIDES HAVE BEEN REVISED RECCOMMENDING LINE OUTAGES FOR END-TO-END CHECK COMMUNICATIONS CHECKS.NO DISC SWITCHING REQUIRED, JUST OPEN PCBSSCOTT HORNER WILL BE AT THE MARION TERMINAL
24-15221 | 16578111 | 12/17/2024 08:00 | 12/17/2024 16:00 | JOHN DAY: PCB 4167 |  | JDAY, NWACI, WOCS, WOJD | Routine Service / John Day
24-02790 | 15045135 | 12/17/2024 08:00 | 12/21/2024 16:00 | JENKINS-SMITHSON SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE | JENKINS-SMITHSON SECTION OF COLUMBIA-ELLENSBURG NO 1 115KV LINE | TCLA | #1482042 REMOVE OLD FIBER FOR THE SCHULTZ-FRANKLIN SECTION OF THE ROSS-SCHULTZ FIBER PROJECT.
24-00031 | 11036036 | 12/17/2024 09:00 | 12/17/2024 17:00 | DWORSHAK PH: PCB XJ-7 | DWORSHAK PH: PCB XJ-7, DWORSHAK PH: PCB XJ-7 |  | #1468496 XJ-7 NEEDS TO BE OPEN DURING CAPABILITY CURVE TESTING OF UNIT 1
24-15825 | 16689250 | 12/17/2024 10:00 | 12/17/2024 10:15 | GRAND COULEE: PCB 2392, GRAND COULEE: PCB 2396 |  | GEN, NOH, WOCN | Bay outage to support removing G-23 from service for commutator stoning.
24-15826 | 16689259 | 12/17/2024 14:15 | 12/17/2024 14:30 | GRAND COULEE: PCB 2392, GRAND COULEE: PCB 2396 |  | GEN, NOH, WOCN | Bay outage to support returning G-23 to service after commutator stoning.
24-10437 | 16579097 | 12/18/2024 08:00 | 12/18/2024 15:00 | LEBANON: PCB B-848 | AIRPORT-LEBANON SECTION OF ALBANY-LEBANON NO 1 115KV LINE | SLAL | ROUTINE SERVICE (ONE MONITOR) | CHECK THAT PACW EAST OF ALBANY LOOP IS INTACT.PCB B-848 CANNOT BE BYPASSED AT PRESENT. WORK ON B-848 FORCES OUT THE AIRPORT - LEBANON SECTION OF THE ALBANY LEBANON #1 115KV LINE. LINE WILL BE OPEN-ENDED DURING THE WORK.
24-13672 | 16361522 | 12/18/2024 08:00 | 12/18/2024 11:00 | PEARL: PCB 4280 |  | SOA, NOPE | TRIP CHECKS TO PCB 4280 | LINE RELAY MAINTENANCE WORK PERMIT = iTOA # 24-13671WE WILL BE ISOLATING PCB 4280 TO TRIP IT FROM BOTH SETS OF PEARL-KEELER #1 LINE RELAYS O.A.T.
24-01471 | 14854142 | 12/18/2024 11:00 | 12/18/2024 15:00 | MARION: PCB 4371 BFR | MARION: PCB 4371 | NWACI, WOCS | SPC TO PERFORM TRIP CHECKS TO PCB 4371 FROM JDAY 1 500KV LINE RELAYS SETS 1 & 2 OAT
24-13673 | 16361504 | 12/18/2024 11:30 | 12/18/2024 14:00 | PEARL: PCB 4283 |  | SOA, NOPE | TRIP CHECKS TO PCB 4283 | LINE RELAY MAINTENANCE WORK PERMIT = iTOA # 24-13671WE WILL BE ISOLATING PCB 4283 TO TRIP IT FROM BOTH SETS OF PEARL-KEELER #1 LINE RELAYS O.A.T.
24-01469 | 14854125 | 12/19/2024 08:00 | 12/19/2024 14:00 | MARION: PCB 4368 BFR | MARION: PCB 4368 | NWACI, WOCS | SPC TO PERFORM TRIP CHECKS TO PCB 4368 FROM JDAY 1 500KV LINE RELAYS SETS 1 & 2 OAT
24-11995 |  | 12/19/2024 08:00 | 12/19/2024 11:00 | MCNARY-COYOTE SPRINGS NO 1 500KV LINE |  | SIG, WOM, WOJD, NWACI | CUT OVER CT CONTRIBUTIONS FOR NEW DFR AND REMOVE FROM OLD OSCILOGRAPH | THIS WORK TO BE DONE IN CONJUNCTION WITH OUTAGE ON THE MCNARY - COYOTE SPRINGS #1 500 KV LINE FOR THE CUT IN TO LONGHORN SUB.
24-12002 | 16361651 | 12/19/2024 08:00 | 12/19/2024 10:00 | KEELER: PCB 4394 |  | SOA, NOPE | TRIP CHECKS TO PCB 4394 | RELATED TO PEARL-KEELER LINE RELAY MAINTENANCE AT KEELER (iTOA # 24-11826)
24-12005 | 16361656 | 12/19/2024 10:05 | 12/19/2024 12:00 | KEELER: PCB 4322 |  | SOA, NOPE | TRIP CHECKS TO PCB 4322 | RELATED TO PEARL-KEELER LINE RELAY MAINTENANCE AT KEELER (iTOA # 24-11826)
24-12006 | 16361676 | 12/19/2024 13:00 | 12/19/2024 15:00 | KEELER: PCB 4763 INCLUDING 500KV CAP GROUP NO 3 |  | WOCS, SOA, NOPE | TRIP CHECKS TO PCB 4763 | 500KV CAP SECTION #3 WILL NOT BE AVAILABLE DURING THESE TRIP CHECKSPLACE AVC SWITCH FOR 500KV REACTIVE GROUP #3 IN MANUALTAKE L/C AND C/O MAINT CUTOUT SWITCHES FOR:REACTIVE RAS AC A (CKT 7F58)REACTIVE RAS AC B (CKT 7F59)RELATED TO PEARL-KEELER LINE RELAY MAINTENANCE AT KEELER (iTOA # 24-11826)
24-16460 | 16737442 | 12/23/2024 07:30 | 12/23/2024 10:30 | MALIN: 500KV REACTOR 2 INCLUDING PCB 4037 | MALIN: PCB 4037, MALIN: 500KV REACTOR 2 | NWACI, COI | B PHASE OIL SAMPLE | WEEKLY 500 KV REACTOR 2 B PHASE OIL SAMPLES TO BE TAKEN WHILE EQUIPMENT IS ISOLATED DUE TO INSTALLED REACTOR BEING SUSPECT EQUIPMENT DUE TO PAST GASSING ISSUES UNTIL DEEMED OTHERWISE.SUDDEN PRESSURE RELAY CUT OUT FOR OIL SAMPLES
24-16461 | 16737467 | 12/30/2024 07:30 | 12/30/2024 10:30 | MALIN: 500KV REACTOR 2 INCLUDING PCB 4037 | MALIN: PCB 4037, MALIN: 500KV REACTOR 2 | NWACI, COI | B PHASE OIL SAMPLE | WEEKLY 500 KV REACTOR 2 B PHASE OIL SAMPLES TO BE TAKEN WHILE EQUIPMENT IS ISOLATED DUE TO INSTALLED REACTOR BEING SUSPECT EQUIPMENT DUE TO PAST GASSING ISSUES UNTIL DEEMED OTHERWISE.SUDDEN PRESSURE RELAY CUT OUT FOR OIL SAMPLES
24-15828 | 16689267 | 12/31/2024 10:00 | 12/31/2024 10:15 | GRAND COULEE: PCB 2492, GRAND COULEE: PCB 2496 |  | GEN, NOH, WOCN | Bay outage to support removing G-24 from service for commutator stoning.
24-15829 | 16689270 | 12/31/2024 14:15 | 12/31/2024 14:30 | GRAND COULEE: PCB 2492, GRAND COULEE: PCB 2496 |  | GEN, NOH, WOCN | Bay outage to support returning G-24 to service after commutator stoning.