## Request List
Request# | CAISO# | Start | End | Main Element Impacted | Elements Involved | Path Affected | Status | Work to be Performed | Additional Notes | Work Type | Nature of Work
21-01711 | 15666227 | 02/03/2021 09:00 | 02/28/2030 17:00 | -USBR- GRAND COULEE 287/230KV TRANSFORMER KX-17-A (OLYMPIA-GRAND COULEE NO 1 287KV LINE OPERATING AT 230KV) | OLYMPIA: 287/230KV TRANSFORMER 3, GRAND COULEE: 287/230KV TRANSFORMER 1 | NOEL, RP, SOC, WOCN, IROL, NOH, OKLA | ACTIVE | #1421102 -USBR WORK-4 YEAR MAINTENANCE ON TRANSFORMER KX-17-A. LINE RETURNED TO SERVICE AT 230KV | 2-No slimsend date changed to match dart, duplicate authorization voided. | Info | OUT_OF_SERVICE
23-04125 | 13016840 | 01/28/2023 17:00 | 09/30/2026 23:59 | ROCKY REACH-MAPLE VALLEY NO 1 345kV LINE OPERATING AT 230KV | ROCKY REACH: 345/230KV TRANSFORMER 1, ROCKY REACH-MAPLE VALLEY NO 1 345kV LINE OPERATING AT 230KV, MAPLE VALLEY: 345/230KV TRANSFORMER 1 | WOCN, SOC/NOEL, CI, GEN, IROL, NOEL, NOH, SOC | ACTIVE | ROCKY REACH-MAPLE VALLEY 1 345KV LINE OPERATING AT 230KV DUE TO MAPLE VALLEY 345/230KV BANK 1 GASSING |  | Info | OUT_OF_SERVICE
23-01684 | 11460660 | 02/03/2023 15:30 | 01/21/2025 09:00 | PG&E -TABLE MOUNTAIN: ROUND MOUNTAIN 1 500KV LINE SERIES CAP 1 | PG&E -TABLE MOUNTAIN: ROUND MOUNTAIN 1 500KV LINE SERIES CAP 1 | COI, NWACI | ACTIVE | OUT_OF_SERVICE | THIS WORK IS PREPARING FOR THE NEW FERN ROAD CAP STATION BETWEEN ROUND MOUNTAIN AND TABLE MOUNTAIN. | Info | OUT_OF_SERVICE
23-03222 | 11461724 | 02/10/2023 18:30 | 01/31/2025 09:00 | PG&E- TABLE MOUNTAIN: ROUND MOUNTAIN 500KV LINE SERIES CAP GROUP 2 | PG&E- TABLE MOUNTAIN: ROUND MOUNTAIN 500KV LINE SERIES CAP GROUP 2 | NWACI, COI | ACTIVE | BUILD AND MAKE READY AN ADDITIONAL SEGMENT FOR CAP BANK # 2 |  | Info | OUT_OF_SERVICE
23-18445 | 14853282 | 12/14/2023 06:40 | 03/31/2025 16:00 | BCH - CHAPMAN: 5CX1 | BCH - CHAPMAN: 5CX1 | NI | ACTIVE | BCH: THEIR WORK |  | Info | OUT_OF_SERVICE
24-03190 | 15142411 | 01/15/2024 18:00 | 01/31/2025 15:00 | ECHO LAKE: 500KV CAP GRP 2 INCLUDING PCB 5127 | ECHO LAKE: PCB 5127, ECHO LAKE: 500KV CAP GROUP 2 | BCHT, NOEL, SOC, WOCN, NI, BCHW, IROL | ACTIVE | BLOWN FUSE ISSUES |  | Control | OUT_OF_SERVICE
24-03188 | 15061704 | 01/15/2024 18:00 | 01/31/2025 15:00 | ECHO LAKE: 500KV CAP GRP 1 INCLUDING PCB 5125 | ECHO LAKE: 500KV CAP GRP 1 INCLUDING PCB 5125, ECHO LAKE: PCB 5125, ECHO LAKE: 500KV CAP GROUP 1 | BCHT, BCHW, NOEL, SOC, WOCN, NI, IROL | ACTIVE | FUSE ISSUES IN THE CAP GRP |  | Control | OUT_OF_SERVICE
24-09008 | 15780159 | 05/06/2024 18:00 | 05/15/2025 15:00 | ROCK CREEK: 230KV CAP GROUP 1 SECTION 1 INCLUDING PCB A-1719 |  |  | ACTIVE |  | MAKE SURE ROCK CREEK: 230KV CAP GROUP 1 SECTION 1 IS LOGGED BACK IN ON ATTACHED INTERRUPTION ENTRY ON RELATED TAB WHEN WORK IS COMPLETED. WAG | Control | OUT_OF_SERVICE
24-13950 |  | 08/16/2024 00:06 | 12/01/2025 17:00 | PG&E - PACIRAS CONTROLLER A |  |  | ACTIVE | PG&E WORK-MOVING RAS CIRCUIT FROM THEIR SF CONTROL CENTER TO NEW LOCATION THE FOLLOWING CIRCUITS WILL REMAIN C/O FOR THE DURATION OF THIS OUTAGE: PACIRAS System 1A from Dittmer (INT: 7325 BPA: 7B72) PACIRAS System 2A from Dittmer (INT: 7327 BPA: 7B74) Cut Out RAS DCA (Celilo T/T) at Dittmer (INT: 7323 BPA: 7E62) |  | Info | OUT_OF_SERVICE
24-05901 | 15358908 | 10/01/2024 08:00 | 02/28/2025 16:00 | WAPA - TRACY: 500KV SHUNT CAPACITOR PT10A & PT10B | WAPA - TRACY: 500KV SHUNT CAPACITOR PT10A & PT10B | COI | ACTIVE | REPLACE SHUNT CAPACITOR BREAKERS 1292 & 1392 |  | Info | OUT_OF_SERVICE
24-16921 |  | 10/23/2024 12:00 | 05/01/2025 23:59 | HEYBURN-MINICO 138KV LINE | HEYBURN: IDAHO POWER CO 138KV FEEDER 1 |  | ACTIVE |  | IDAHO OWNS THIS ENTIRE LINE EXCEPT FOR TWO SPANS OWNED BY BPA, WHICH ARE NOW THE LIMITING ELEMENTS.LIMIT (102.8MVA) THAT IDAHO, BPA, AND RC ARE USING FOR STUDY IS DIFFERENT FROM WHAT IS SHOWN IN FRR, USE THE 102.8MVA LIMIT UNTIL THE 2 BPA SPANS ARE REPLACED (SUPPOSED TO HAPPEN IN EARLY 2025)CONTACT TOOP, JAMES WONG, PRIOR TO EXTENDING/COMPLETING THIS REQUEST.SCADA LIMITS HAVE BEEN ENTERED AS TEMP LIMITS TO PREVENT THEM FROM BEING OVERRIDDEN AUTOMATICALLY BY AN UPDATE. | Derate | EQUIPMENT_DERATE
24-17059 | 16817941 | 10/25/2024 01:00 | 06/30/2025 16:00 | WAUTOMA: SCHULTZ 1 500KV LINE SERIES CAP GROUP NO 1 |  | NOH, WOCN | ACTIVE | TROUBLESHOOT AND REPAIR CAP GROUP AFTER STAGED FAULT TESTING (GROUNDED CLEARANCE) | PER MANUFACTURER/ DISTRICT - CANNOT PLACE THESE CAPS BACK IN SERVICE UNTIL FAULT TESTING COMPLETED. RPT | Control | OUT_OF_SERVICE
24-13394 | 16799234 | 11/18/2024 08:00 | 01/17/2025 17:00 | MCNARY-B-1345 SECTION OF THE MCNARY-BADGER CANYON NO 1 115KV LINE INCLUDING THE PLYMOUTH TAP BC-165 AND PLYMOUTH TAP 2 BC-495 DISC | MCNARY: PCB B-980, MCNARY-B-1345 SECTION OF MCNARY-BADGER CANYON NO 1 115KV LINE, PLYMOUTH TAP TO MCNARY-BADGER CANYON NO 1 115KV LINE | GEN, LOAD, WOM, TCLA | UNDER REVIEW | REMOVE WOOD STRUCTURES FROM 1/6-1/9 AND CONDUCTORS FROM STRUCTURES 1/5-1/10, INSTALL NEW POLES FROM 1/6-1/11, STRING NEW CONDUCTOR FROM 1/5-1/12, TC9 TOWER REINFORCEMENT AND INSTALL NEW CONDUCTOR FROM DEAD END STRUCTURE 0/1-TOWER TC9 | STEP 6: REMOVE WOOD STRUCTURES FROM 1/6-1/9 AND CONDUCTORS FROM STRUCTURES 1/5-1/10STEP 7: INSTALL NEW POLES FROM 1/6-1/11 AND STRING NEW CONDUCTOR FROM 1/5-1/12STEP 8: TC9 TOWER REINFORCEMENTSTEP 9: INSTALL TRANSMISSION LINE FROM 0/1-TC9CLEARANCE LIMITS:B-1345 LSD, (NEW) B-2149 LSD, BENTON PUD'S BC-187, MCNARY'S B-980 L/S AND A/B DISC. MCNARY OPS TO WORK WITH BENTON COUNTY PUD ON MCC'S BEHALF TO PICKUP CLEARANCE ON THEIR BC-187 TERMINAL | Clearance | OUT_OF_SERVICE
24-14261 | 16813250 | 12/11/2024 08:00 | 01/24/2025 15:00 | RINGOLD-MESA SECTION OF BENTON-SCOOTENEY NO 1 115KV LINE |  | TCLA | UNDER REVIEW | COMPLETE LINE REBUILD |  | Clearance | OUT_OF_SERVICE
24-15491 | 16806723 | 12/16/2024 08:00 | 01/17/2025 15:00 | MCNARY-B-1345 SECTION OF THE MCNARY-BADGER CANYON NO 1 115KV LINE INCLUDING THE PLYMOUTH TAP BC-165 DISC | PLYMOUTH TAP TO MCNARY-BADGER CANYON NO 1 115KV LINE, MCNARY: PCB B-980, MCNARY-B-1345 SECTION OF MCNARY-BADGER CANYON NO 1 115KV LINE | TCLA, GEN, WOM, LOAD | UNDER REVIEW | PROXIMITY WORK TO INSTALL NEW MCNARY-BERRIAN #1 115KV TRANSMISSION LINE FROM 0/1-TC 9 | GROUND SWITCH 7472 REQUESTED CLOSED CLEARANCE LIMITS:B-1345 LSDB-980 L/S AND A/B DISCBC-187 FROM BENTON COUNTY PUDCONTACT INFO:FORSMANN 971-678-6878 | Clearance | OUT_OF_SERVICE
24-00924 | 16813588 | 12/30/2024 07:00 | 01/31/2025 17:00 | MCNARY: 115KV AUX BUS INCLUDING B-979 A/B DISC | MCNARY: PCB B-988, MCNARY: 115KV AUX BUS |  | APPROVED | INSTALL NEW MCNARY-BERRIAN #1 115KV TRANSMISSION LINE FROM 0/1-TC 9 | CLEARANCE LIMITS:B-978, B-980, B-986, B-988, B-990, B-987, B-994, B-995, B-997 A/B AND B-979 L/S DISCONNECTS | Clearance | OUT_OF_SERVICE
24-17137 | 16835232 | 12/30/2024 08:00 | 01/03/2025 16:00 | FAIRGROUNDS-ST HELENS SECTION OF ST JOHNS-ST HELENS NO 1 115KV LINE |  | LOAD, SOA, NOPE | UNDER REVIEW | PGE WORK, POLE REPLACEMENT |  | Clearance | OUT_OF_SERVICE
24-10447 | 16187838 | 01/06/2025 06:00 | 01/17/2025 17:00 | GRIZZLY: PCB 5025 |  | NWACI | UNDER REVIEW | REPLACE PCB 5025 SEL-BFR |  | Work Permit | OUT_OF_SERVICE
25-00700 | 16812664 | 01/06/2025 06:00 | 01/06/2025 20:00 | OLYMPIA: 230KV WEST AUX BUS | OLYMPIA: PCB A-216 | NOEL, RP, SOC, WOCN | UNDER REVIEW | REMOVE A-222 AND A-216 A/B RISERS SECTIONS FROM THE 230KV A/B UP TO THE OPEN SIDE OF A-222 AND A-216 A/B DISCONNECTS | SEE RELATED ITOA #25-00710 AND 25-00706 FOR TAGGING THE REMOVED BUS PARTS. | Clearance | OUT_OF_SERVICE
24-00128 | 14702032 | 01/06/2025 07:00 | 02/07/2025 15:00 | MCNARY-COYOTE SPRINGS NO 1 500KV LINE, INCLUDING NEW LONGHORN SUB | MCNARY: PCB 4231, MCNARY: PCB 4234, COYOTE SPRINGS: PCB 5184, COYOTE SPRINGS: PCB 5187 | SIG, WOM, WOJD, NWACI, WOLM | UNDER REVIEW | REMOVE TEMPORARY WIRE, DEMO OLD STEEL STRUCTURES, DROP CONDUCTOR INTO LONGHORN SUB. | LONGHORN CONSTRUCTION PROJECT. PART OF LINE CONSTRUCTION TO SPLIT THE EXISTING MCNARY-COYOTE SPRINGS #1 500KV LINE AND DROP INTO NEW LONGHORN SUBSTATION. AT END OF LINE CONSTRUCTION IN OCTOBER 2024 WILL HAVE MCNARY-LONGHORN #1 500KV LINE & LONGHORN-COYOTE SPRINGS #1 500KV LINE.JUNE 2024 OUTAGE: TRANSMISSION LINE CREWS WILL BE TOPPING THE 500KV LATTICE TOWERS & TRANSFERRING CONDUCTOR TO NEW TOWERS.SEPTEMBER 2024 OUTAGE: TRANSMISSION LINE CREWS WILL BE REMOVING TEMPORARY SPAN OF WIRE, DEMO STEEL STRUCTURES, TOP STEEL STRUCTURES, INSTALL CONDUCTOR INTO LONGHORN SUBSTATION, INSTALL OVERHEAD GROUND WIRE.CL LIMITSMCNARY: MOD'S 4232 & 4233. NO GROUND SWITCH AT MCNARY TERMINALCOYOTE SPRINGS: MOD'S 5185 & 5186. GROUND SWITCH 7226 TO BE CLOSED. | Clearance | OUT_OF_SERVICE
24-11305 | 16048756 | 01/06/2025 07:00 | 01/16/2025 15:00 | ALLSTON: PCB 4500, BFR |  | SOA, NOPE | UNDER REVIEW | REPLACE SEL BFR WITH SEL-352 | REPLACE SEL-BFR with SEL-352 will need to cutout Napavine Line LOR and NB LOR multiple times to remove equipment and perform trip checks. Will trip from 500kV Dead Bus Clearing LOR. Will need to perform in-service checks at conclusion.WO#599028 | Work Permit | OUT_OF_SERVICE
25-00251 | 16192554 | 01/06/2025 08:00 | 01/16/2025 15:00 | ASHE: PCB 4940 BFR | ASHE: PCB 4940 | NWACI, WOCS, WOJD, WOM, FCRPS | UNDER REVIEW | REPLACE BFR | REPLACE PCB 4940 SEL-BFR WITH AN SEL-352. THIS IS AN URGENT REQUEST AS SEL-BFR RELAYS HAVE A HIGH FAILURE RATE. | Work Permit | OUT_OF_SERVICE
25-00117 | 15575890 | 01/06/2025 08:00 | 01/06/2025 15:00 | JOHN DAY-MARION NO 1 5OOKV LINE INCLUDING JOHN DAY: PCB 4167 | JOHN DAY-MARION NO 1 500KV LINE, JOHN DAY: PCB 4167 | NWACI, SIG, WOCS, WOJD, PDCI, JDAY | UNDER REVIEW | REMOVE BUS BETWEEN MOD 4168 AND MARION #1 500 KV LINE FOR MOD REPLACEMENT |  | Clearance | OUT_OF_SERVICE
25-00114 | 15651209 | 01/06/2025 08:00 | 01/09/2025 15:00 | GARRISON-TAFT #2 500KV LINE INCLUDING TAFT: PCB'S 4125 AND 4148 | TAFT: PCB 4125, TAFT: PCB 4148, GARRISON-TAFT NO 2 500KV LINE, GARRISON: TAFT 2 500KV LINE SERIES CAP GROUP 2 | MT-NW, WOH, SIG | UNDER REVIEW | DISCONNECT MAINT ON MODS 4126, 4146, 4147 | Sub maintenance requests this time of year due to the work being inside, I spoke with the Forman 3, and he is aware that the work may get canceled last minute due to system configuration or weather. | Clearance | OUT_OF_SERVICE
24-13540 | 16798578 | 01/06/2025 08:00 | 01/06/2025 13:00 | SIFTON: SIFT-NBON CKT 7A21 & SIFT-ROSS CKT 7A23 TT | SIFTON TAP TO NORTH BONNEVILLE-ROSS NO 1 230KV LINE, NORTH BONNEVILLE: PCB A-13, ROSS: PCB A-34, SIFTON: PCB A-163, BONNEVILLE PH 1-NORTH BONNEVILLE NO 1 230KV LINE | GEN, LOAD, SOA, WOCS, NOPE, FCRPS | UNDER REVIEW | ANNUAL TRANSFER TRIP MAINTENANCE | ONLY ONE SET OF TRANSFER TRIP AT EACH TERMINAL, (NON-REDUNDANT).3 TERMINAL LINE, MCC DISPATCH TO OPEN ALL BREAKERS DE-ENERGIZING THE LINE FOR DURATION OF OUTAGE.SIFTON IS BACK-TO-BACK WITH NBON & ROSS. OPERATOR TO BE AT ALL 3 TERMINALS TO C/O TT.PSC TO BE AT ALL 3 TERMINALS TO MAINTAIN TT. NBON & ROSS PSC TO WORK UNDER PATTONS WORK PERMIT AT SIFTON.AFFECTED CIRCUITS: SIFT-NBON CKT 7A21SIFT-ROSS: CKT 7a23CONTACT LIST:DE: BRANDON MARTIN (509-939-2937)WP HOLDER/ CRAFTSMAN: JOHN PATTON (360-418-8113)CRAFTSMAN: JEFF MILONAS: (360-418-8162) | Work Permit | COMMUNICATIONS
25-00104 | 15629193 | 01/06/2025 08:00 | 01/06/2025 15:00 | MARION: PCB 4368 |  | NWACI, WOCS | UNDER REVIEW | Routine Service | THIS IS A TIE PCB WITH RECLOSING NORMALLY C/O | Clearance | OUT_OF_SERVICE
25-00160 | 15916558 | 01/06/2025 08:00 | 01/06/2025 15:00 | ASHE: PCB 5466 |  | NWACI, WOJD, WOM, WOS, FCRPS | UNDER REVIEW | PCB ROUTINE SERVICE AND FIX B PHASE CABINET HEATER. | PRIORITY 2 WORK WITH A DUE DATE OF 1/20/25. | Clearance | OUT_OF_SERVICE
25-00235 | 16209996 | 01/06/2025 09:00 | 01/06/2025 12:00 | MCNARY: 500/230KV TRANSFORMER 1 INCLUDING PCB'S 4228 AND 4231 | MCNARY: 500/230KV TRANSFORMER 1, MCNARY: PCB 4228, MCNARY: PCB 4231 | WOM, NWACI | UNDER REVIEW | CUT OVER CT CONTRIBUTIONS TO THE NEW DFR AND REMOVE FROM THE OLD OSCILOGRAGPH | PCB WILL BE ISOLATE AND CT'S SHORTED AT THE TERM FRAME AND CUT OVER TO THE NEW DFR. | Work Permit | OUT_OF_SERVICE
25-00605 | 16812761 | 01/07/2025 06:00 | 01/07/2025 20:00 | OLYMPIA: 230KV WEST MAIN BUS | OLYMPIA: PCB A-222, OLYMPIA: PCB A-220, OLYMPIA: PCB A-218, OLYMPIA: PCB A-216, OLYMPIA-SATSOP NO 2 230KV LINE, CHEHALIS-OLYMPIA NO 1 230KV LINE, OLYMPIA: 230/115KV TRANSFORMER 1, OLYMPIA: 230KV CAP GROUP 2 SECTION 1, OLYMPIA: 230KV CAP GROUP 2 SECTION 2, OLYMPIA-SHELTON NO 4 230KV LINE | RP, LOAD, NOEL, SI, SOC, WOCN, SOA, NOPE | UNDER REVIEW | CUT FREE AND REMOVE M/B RISER SECTIONS BETWEEN A-222 AND A-216 M/B DISCONNECTS AND THE 230 KV M/B | STATION SERVICE IS CURRENTLY BEING FED FROM 230/115KV XFMR BANK 2230/15KV XFMR BK #2 WILL REMAIN IN SERVICEOLYMPIA-SATSOP #2 WILL BE FORCED OUT DUE TO LOSS OF M/B PT'SOLYMPIA-SHELTON NO 4 230KV LINE DUE TO LOSS OF M/B PT'S 230 CAP GROUP 1 SECTIONS 1 AND 2 WILL BE FORCED OUT DUE TO LOSS OF M/B PT'S230 WEST BUS TIE AND OLYMPIA-SATSOP NO.2 WILL BE CUT FREE AND OOS UNTIL BREAKER REPLACEMENTS ARE COMPLETEDSEE RELATED ITOA #25-00710 AND 25-00706 FOR TAGGING THE REMOVED BUS PARTS. | Clearance | OUT_OF_SERVICE
24-17147 | 16841642 | 01/07/2025 07:00 | 01/07/2025 14:00 | CONKELLEY: 230KV EAST MAIN BUS | FLATHEAD-CONKELLEY #1 230KV LINE, COLUMBIA FALLS-CONKELLEY NO 1 230KV LINE, HUNGRY HORSE-CONKELLEY NO 1 230KV LINE, CONKELLEY: 230/13.8KV TRANSFORMER 4 | MT-NW, FLAT, GEN, LOAD, FCRPS | UNDER REVIEW | SEPARATE MAIN BUS BETWEEN A-1284 AND A-1286 POSITIONS | SEPARATE 230KV EAST MAIN BUS BETWEEK A-1284 AND A-1286 POSITIONS.TRUMBULL CREEK WILL BE FED RADIALLY FROM FLATHEAD.STATION SERVICE WILL BE TRANSFERED TO EG FOR THE DURATION. | Clearance | OUT_OF_SERVICE
25-00725 | 16835720 | 01/07/2025 07:00 | 01/07/2025 17:00 | ICE HARBOR-FRANKLIN NO 1 115KV LINE |  | GEN, TCLA | APPROVED | Bus Section 1 Outage to remove links in Bus Section in preparation of XW2 Breaker Rebuild. Disconnect B1492 and B1495 will be Open. Line can remain Energized. |  | Info | OUT_OF_SERVICE
25-00237 |  | 01/07/2025 08:00 | 01/07/2025 12:00 | MCNARY: 500/230KV TRANSFORMER BANK #2 INCLUDING PCB'S 5198 AND 5204 | MCNARY: 500/230KV TRANSFORMER 2, MCNARY: PCB 5198, MCNARY: PCB 5204 | WOM, NWACI | UNDER REVIEW | CUT OVER THE CT CONTRIBUTIONS TO THE NEW DFR AND REMOVE THE OLD WIRING TO THE OSCILOGRAPH | CT'S WILL BE SHORTED AT THE TERM FRAME AND CUT OVER TO THE NEW DFR | Work Permit | OUT_OF_SERVICE
25-00162 | 15916564 | 01/07/2025 08:00 | 01/07/2025 15:00 | ASHE: PCB 5463 |  | NOH, NWACI, FCRPS | UNDER REVIEW | PCB ROUTINE SERVICE. | PRIORITY 2 WORK WITH A DUE DATE OF 1/20/25. | Clearance | OUT_OF_SERVICE
25-00106 | 15583027 | 01/07/2025 08:00 | 01/07/2025 15:00 | SANTIAM: 230KV REACTIVE GROUP 1 REACTOR 1 INCLUDING PCB A-504 | SANTIAM: 230KV REACTIVE GROUP 1 REACTOR 1, SANTIAM: PCB A-504 | SLAL, NWACI | UNDER REVIEW | Routine Service |  | Clearance | OUT_OF_SERVICE
24-13579 | 16799785 | 01/07/2025 08:00 | 01/07/2025 13:00 | SIFTON: SIFT-NBON CKT 7A22 & SIFT-ROSS CKT 7A24 TT | SIFTON TAP TO NORTH BONNEVILLE-ROSS NO 2 230KV LINE, ROSS: PCB A-22, NORTH BONNEVILLE: PCB A-14, SIFTON: PCB B-1511, SIFTON: 230KV WEST MAIN BUS, SIFTON: 230KV AUX BUS, SIFTON: 230/115KV TRANSFORMER 1, NORTH BONNEVILLE-ROSS NO 2 230KV LINE | GEN, SOA, WOCS, LOAD, NOPE, FCRPS | UNDER REVIEW | ANNUAL PDR 2000 TRANSFER TRIP MAINTENANCE | ONLY ONE SET OF TRANSFER TRIP AT EACH TERMINAL, (NON-REDUNDANT).3 TERMINAL LINE, MCC DISPATCH TO OPEN ALL BREAKERS DE-ENERGIZING THE LINE FOR DURATION OF OUTAGE.SIFTON STATION SERVICE TO TRANSFER FROM PRIMARY TO ALTERNATE SOURCE (CLARK PUD) FOR DURATION OF OUTAGE.SPC REQUESTS XFMR NO.1 AT SIFTON TO STAY DE-ENERGIZED DUE TO CREATING HARMONICS ON CLARK PUD'S SYSTEM.SIFTON IS BACK-TO-BACK WITH NBON & ROSS, OPERATOR TO BE AT ALL 3 TERMINALS TO C/O TT.PSC TO BE AT ALL 3 TERMINALS TO MAINTAIN TT. NBON & ROSS PSC TO WORK UNDER PATTONS WORK PERMIT AT SIFTON.BPA AFFECTED CIRCUITS: SIFTON-NORTH BONNEVILLE CKT 7A22, SIFTON-ROSS CKT 7A24.CONTACT LIST:BRANDON MARTIN: (509) 939-2937JOHN PATTON: (360) 418-8113JEFF MILONAS: (360) 418-8162 | Work Permit | OUT_OF_SERVICE
25-00874 | 16821873 | 01/07/2025 10:00 | 01/07/2025 10:15 | GRAND COULEE: PCB 2192, GRAND COULEE: PCB 2196 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support removing G-21 from service for commutator stoning. |  | Info | OUT_OF_SERVICE
25-00875 | 16821887 | 01/07/2025 14:15 | 01/07/2025 14:30 | GRAND COULEE: PCB 2192, GRAND COULEE: PCB 2196 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support returning G-21 to service after commutator stoning. |  | Info | OUT_OF_SERVICE
25-00710 | 16840870 | 01/08/2025 06:00 | 04/29/2025 16:00 | OLYMPIA: PCB A-216 |  | NOEL, RP, SOC, WOCN | UNDER REVIEW | REPLACE PCB A-216 AND A-216 M/B AND A/B DISCONNECTS | ISSUED AGAINST DISPATCH DO NOT OPERATE TAGSSEE RELATED ITOA #'S 25-00700 & 25-00605 FOR OUTAGES TO REMOVE THE BUS PARTS | Clearance | OUT_OF_SERVICE
25-00706 | 16841248 | 01/08/2025 06:00 | 03/25/2025 15:00 | OLYMPIA-SATSOP NO 2 230KV LINE INCLUDING PCB A-222 | OLYMPIA-SATSOP NO 2 230KV LINE, OLYMPIA: PCB A-222 | LOAD, SI, RP, NOEL, SOC, WOCN | UNDER REVIEW | REPLACE PCB A-222 INCLUDING M/B, L/S AND A/B DISCONNECTS | ISSUED AGAINST DISPATCH DO NOT OPERATE TAGSSEE RELATED ITOA #'S 25-00700 & 25-00605 FOR OUTAGES TO REMOVE THE BUS PARTS | Clearance | OUT_OF_SERVICE
25-00728 | 16835832 | 01/08/2025 07:00 | 01/09/2025 17:00 | ICE HARBOR-SACAJAWEA SECTION OF ICE HARBOR-FRANKLIN NO 2 115KV LINE |  | TCLA | APPROVED | Bus Section 2 Outage to Remove XW2 Breakers For Rebuild. Disconnect B1493 will be Open. Line can remain Energized. | 1493 disconnect opened due to proximity of XW2 for their work. | Info | OUT_OF_SERVICE
25-00838 | 16807858 | 01/08/2025 07:30 | 01/09/2025 15:30 | ROSS: 230/115KV TRANSFORMER 1 | ROSS: PCB A-26, ROSS: PCB B-2, ROSS: 13.2KV PCB L-25 | LOAD, SOA, NOPE | UNDER REVIEW | PRC RELAY MAINTENANCE /ACCESSORY SERVICE / OIL LEAKS | TRANSFER PRIMARY STATION SERVICE (PCB L-25 TO ALTERNATE SOURCE PCB L-27) PRIOR TO DE-ENERGIZING XFMR NO.1OPERATIONS TO NOTIFY ANDREW WILKES THAT DITTMER RUNNING ON ALTERNATE XFMR NO.3 SOURCE FOR DURATION OF OUTAGE.CLEARANCE LIMITS: A-26 XFMR SIDE & A/B DISC'S, B-2 XFMR SIDE & A/B DISC'S, L-25 XFMR SIDE DISC. | Clearance | OUT_OF_SERVICE
24-00247 | 13975578 | 01/08/2025 08:00 | 01/08/2025 16:00 | SANTIAM-ALBANY NO. 1 230KV LINE INCLUDING SANTIAM: PACW 230/69KV TRANSFORMER 2, 230KV LBD A-538, AND 230KV AUX BUS | SANTIAM-ALBANY NO 1 230KV LINE, SANTIAM: 230KV AUX BUS, SANTIAM: PACW 230/69KV TRANSFORMER 2, SANTIAM: LBD A-538, SANTIAM: PCB A-514, SANTIAM: 69KV PCB L-1114, ALBANY: 230/115KV TRANSFORMER 1, ALBANY: PCB B-520 | SLAL, NWACI, SCORC | UNDER REVIEW | COMPLETE SERVICES A-514 AUX BUS & A-539 LINE SECTIONALIZING DISCONNECTS | UNGROUNDED AT ALBANY AND SANTIAM TERMINALS REQUESTED BY SALEM SUB MAINTENANCE.PRIOR TO ANY SWITCHING:PACW MUST SWITCH ON THEIR 69KV SYSTEM TO PROVIDE LONG-LINE FOR SANTIAM: 69KV PACW FDR 1 & 69KV CPI FDR 1 OVER SANTIAM 69KV MAIN BUS - PACW GENERALLY REQUESTS GEN DROP SCHEME C/O FOR SANTIAM PCB L-1116 DURING THIS CONFIGURATION.SANTIAM STATION SERVICE NOT EFFECTED.13 CLEARANCE LIMITS:Albany: A-95Santiam: L-1114 T/S & A/B, A-514 L/S, A-516 A/B, A-524 A/B, A-528 A/B, A-530 A/B, A-532 A/B, A-534 A/B, A-536 A/B, A-540 A/B, A-542 A/B Disconnects. | Clearance | OUT_OF_SERVICE
25-00238 | 16210088 | 01/08/2025 08:00 | 01/08/2025 11:00 | MCNARY-JOHN DAY NO 2 500KV LINE INCLUDING MCNARY PCB'S 5217 AND 5211 | MCNARY-JOHN DAY NO 2 500KV LINE, MCNARY: PCB 5211, MCNARY: PCB 5217 | WOM, WOS, WOCS, NWACI, PDCI, WOJD | UNDER REVIEW | CUT OVER CT CONTRIBUTIONS TO THE NEW DFR AND REMOVE THE WIRING FOR THE OLD OSCILOGRAPH | CT'S TO BE SHORTED AT THE TERM FRAME AND THEN CUT OVER TO THE NEW DFR. | Work Permit | OUT_OF_SERVICE
25-00239 | 16201167 | 01/08/2025 12:00 | 01/08/2025 16:00 | MCNARY: PCB'S 5211 AND 5214 (OPEN ENDS LOWER MONUMENTAL-MCNARY NO 1 500KV LINE) | MCNARY: PCB 5211, MCNARY: PCB 5214, SACAJAWEA-MCNARY SECTION OF LOWER MONUMENTAL-MCNARY NO 1 500KV LINE | WOCS, WOJD, WOM, NWACI, GEN, SIG, WOLM, FCRPS | UNDER REVIEW | CUT OVER CT CONTRIBUTIONS TO THE DFR AND REMOVE WIRING TO OLD OSCILOGRAPH | CT'S TO BE SHORTED AT THE TERM FRAME AND CUT OVER TO THE NEW DFR. LINE WILL BE OPEN ENDED AT MCNARY | Work Permit | OUT_OF_SERVICE
24-00248 | 13990438 | 01/09/2025 08:00 | 01/09/2025 16:00 | TUMBLE CREEK-SANTIAM SECTION OF JONES CANYON-SANTIAM NO. 1 230KV LINE INCLUDING SANTIAM: 230KV AUX BUS AND PCB A-528 | TUMBLE CREEK-SANTIAM SECTION OF JONES CANYON-SANTIAM NO 1 230KV LINE, SANTIAM: 230KV AUX BUS, SANTIAM: PCB A-528, SANTIAM: PCB A-530 | GEN, WOCS, WOM, SLAL, SCORC, NWACI | UNDER REVIEW | A-528 LINE SIDE & AUX BUS DISCONNECT COMPLETE SERVICES. | UNGROUNDED CLEARANCE REQUESTEDA-528 GEN DROP SCHEME TO BE C/O PRIOR TO OPENING PCB A-528, AND WILL REMAIN C/O FOR THIS OUTAGE.OPERATIONS WILL BEGIN BY CUTTING OUT A-528 GEN DROP SCHEME AT SANTIAM THEN HEAD TO TUMBLE CREEK TO BREAK LOOP (AND TAG) A-457 LINE SECTIONALIZING DISCONNECT.SPECIAL POWER FLOW STUDY NOT REQUIRED PRIOR TO OPENING TUMBLE CREEK DISCONNECT A-457, AS LONG AS GENERATION AT JONES CANYON IS AT ZERO.11 TOTAL CLEARANCE LIMITS:TUMB: A-457SANT: A-528 M/B, A-514 A/B, A-516 A/B, A-524 A/B, A-530 A/B, A-532 A/B, A-534 A/B, A-536 A/B, A-540 A/B, A-542 A/B DISCONNECTS. | Clearance | OUT_OF_SERVICE
25-00854 | 16813120 | 01/13/2025 07:30 | 02/06/2025 15:30 | ROSS: 230KV CAP GROUP 2 SECTION 3 INCLUDING LBD A-27 | ROSS: LBD A-27, ROSS: 230KV CAP GROUP 2 SECTION 3 | SOA, NOPE | UNDER REVIEW | INSTALL NEW HIGH SECURITY FENCE ALONG 230KV CAP GROUP 2 SECTION 3. | CLEARANCE LIMIT: A-27 REACTIVE BUS DISC.LBD A-27 ON L/C, CAP GROUP 2 SECTION 3 AVC TO MANUAL FOR DURATION OF OUTAGE.IN ADDITION TO THIS OUTAGE, PLACE 230KV CAP GROUP 2 SECTIONS 1 AND 2 AVC'S TO MANUAL DAILY FOR THIS WORK, SEE INFO TAG: 25-00855 | Clearance | OUT_OF_SERVICE
25-00115 | 15613679 | 01/13/2025 08:00 | 01/16/2025 15:00 | TAFT: PCB 4125 |  | MT-NW, WOH | UNDER REVIEW | DIAGNOSTIC SERVICE |  | Clearance | OUT_OF_SERVICE
25-00167 |  | 01/13/2025 08:00 | 01/31/2025 18:00 | SCL - EAST PINE-SOUTH 230KV LINE |  | SOC/NOEL | RECEIVED | SCL WORK: BANK 96 REPLACEMENT |  | Info | OUT_OF_SERVICE
25-00165 |  | 01/13/2025 08:00 | 01/31/2025 18:00 | SCL- EAST PINE 230KV BUS 1, BANK 96 AND SOUTH-EAST PINE 230KV LINE | EAST PINE (SCL)-SOUTH 230KV LINE | NOEL, SOC | UNDER REVIEW |  |  | Info | OUT_OF_SERVICE
25-00156 | 15916623 | 01/13/2025 09:00 | 01/13/2025 15:00 | CHIEF JOSEPH: A-588 BUS SECTIONALIZING BREAKER FAILURE RELAY |  |  | UNDER REVIEW | BREAKER FAILURE RELAY MAINTENANCE, IN SERVICE AND TRIP CHECKS TO A-588 AND LOR 86BD2 S1/S2. TRIP CHECKS FROM 86BD1 S1/S2. | PCB A-588 TO BE ISOLATED, POSITION BYPASSED OVER A/B SECTIONALIZING MOD A-589 | Work Permit | OUT_OF_SERVICE
25-00607 | 16689421 | 01/14/2025 10:00 | 01/14/2025 10:15 | GRAND COULEE: PCB 1992, GRAND COULEE: PCB 1996 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support removing G-19 from service for commutator stoning. |  | Info | OUT_OF_SERVICE
25-00608 | 16689459 | 01/14/2025 14:15 | 01/14/2025 14:30 | GRAND COULEE: PCB 1992, GRAND COULEE: PCB 1996 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support returning G-19 to service after commutator stoning. |  | Info | OUT_OF_SERVICE
25-00053 | 14565872 | 01/15/2025 06:00 | 01/15/2025 17:00 | GRAND COULEE: PCBS 7182 AND 7382 | GRAND COULEE: PCB 7382, GRAND COULEE: PCBS 7182 AND 7382, GRAND COULEE: PCB 7182 | GEN, NOH, WOCN | APPROVED | Land Line Circuit 3 trip circuits for G17. Perform functional testing. |  | Info | OUT_OF_SERVICE
25-00532 | 16820250 | 01/16/2025 07:00 | 01/16/2025 16:00 | BETTAS ROAD-COLUMBIA NO 1 230KV LINE INCLUDING COLUMBIA PCB A-341 AND BETTAS ROAD PCB'S A-3050 & A-3043 | COLUMBIA: PCB A-341, BETTAS ROAD: BETTAS ROAD: PCB A-3050, BETTAS ROAD: PCB A-3043, BETTAS ROAD-COLUMBIA NO 1 230KV LINE | WOCN, NOH, NOEL, SOC, CI, IROL | UNDER REVIEW | ISOLATE THE BETTAS ROAD - COLUMBIA #1 230KV LINE INCLUDING COLUMBIA PCB A-341 AND BETTAS ROAD PCBs A-3043 AND A-3050 FOR END-TO-END TRIP CHECKS | ISOLATE THE BETTAS ROAD - COLUMBIA #1 230KV LINE INCLUDING COLUMBIA PCB A-341 AND BETTAS ROAD PCBs A-3043 AND A-3050 FOR END-TO-END TRIP CHECKS | Work Permit | OUT_OF_SERVICE
25-00729 | 16836091 | 01/16/2025 07:00 | 01/16/2025 17:00 | ICE HARBOR-SACAJAWEA SECTION OF ICE HARBOR-FRANKLIN NO 2 115KV LINE |  | TCLA | APPROVED | Bus Section 2 Outage to Install XW2 Breakers For Rebuild. Disconnect B1493 will be Open. Line can remain Energized. | 1493 disconnect opened due to proximity of XW2 for their work. | Info | OUT_OF_SERVICE
25-00184 | 16208771 | 01/16/2025 08:00 | 01/16/2025 10:00 | HATWAI: PCB 4700 |  | MT-NW, NOH, WOH, WOLM | UNDER REVIEW | PERFORM PCB CLOSE OPERATIONS ASSOCIATED WITH AUTO SYNC/CLOSE RELAY MAINTENANCE. |  | Work Permit | OUT_OF_SERVICE
24-01923 | 14887595 | 01/16/2025 08:00 | 01/16/2025 15:00 | MARION: PCB 4020 | MARION: 500KV REACTOR 2 | NWACI | UNDER REVIEW | ROUTINE 4020 BFR & DIFFERENTIAL RELAY MAINTENANCE (WITH PCB ISOLATED), FOLLOWED BY TRIP CHECKS |  | Work Permit | OUT_OF_SERVICE
25-00185 | 16208816 | 01/16/2025 10:00 | 01/16/2025 12:00 | HATWAI: PCB 4708 |  | MT-NW, NOH, WOH, WOLM | UNDER REVIEW | PERFORM PCB CLOSE OPERATIONS ASSOCIATED WITH AUTO SYNC/CLOSE RELAY MAINTENANCE. |  | Work Permit | OUT_OF_SERVICE
25-00186 | 16208844 | 01/16/2025 12:00 | 01/16/2025 14:00 | HATWAI: PCB 4710 |  | MT-NW, NOH, WOH, WOLM | UNDER REVIEW | PERFORM PCB CLOSE OPERATIONS ASSOCIATED WITH AUTO SYNC/CLOSE RELAY MAINTENANCE. |  | Work Permit | OUT_OF_SERVICE
25-00970 | 16862749 | 01/16/2025 15:00 | 01/16/2025 17:00 | ALLSTON: PCB 4502 |  | SOA, NOPE | UNDER REVIEW | PCB 4502 NEEDS TO BE OPENED UPON RESTORE OF PCB 4500 (#24-11305) IN ORDER TO PERFORM BFR INSERVICE CHECKS. |  | Info | OUT_OF_SERVICE
24-11120 | 16072993 | 01/21/2025 07:00 | 01/31/2025 16:00 | CUSTER: 4272 BFR | CUSTER: PCB 4272 | BCHT, BCHW, NOEL, SOC, NI | UNDER REVIEW | REMOVE BFR AND WIRE, TEST, TRIP CHECKS AND IN SERVICE CHECKS FOR REPLACEMENT BFR | TIME RESTRICTED REQUEST TO REPLACE ALL SEL BFRS BEFORE 2025 START. OLD SEL BFR UNWIRED AND REMOVED. REPLACEMENT SEL-352 BFR WIRED, SET AND TESTED. TRIP CHECKS TO PCB AND BFR LOR ONLY. WORK MAY EXTEND TO FRIDAY. | Work Permit | RELAY_WORK
25-00730 | 16841917 | 01/21/2025 07:00 | 01/22/2025 17:00 | FRANKLIN: B-1528 TERMINAL OF ICE HARBOR-FRANKLIN NO1 115KV LINE | ICE HARBOR-FRANKLIN NO 1 115KV LINE, FRANKLIN: PCB B-1528 | GEN, TCLA | APPROVED | Line 1 Outage for maintenance on Line disconnect B1492 and reinstall bus section 1 links. |  | Clearance | OUT_OF_SERVICE
25-00788 | 16856664 | 01/21/2025 07:30 | 01/21/2025 16:00 | WARREN TAP TO ST JOHNS-ST HELENS #1 115KV LINE INCLUDING WARREN 115/34.5KV TRANSFORMER #1 AND CRPUD TARBELL 115KV FEEDER #1 | WARREN: 115/34.5KV TRANSFORMER 1, WARREN: 34.5KV PCB L-680, WARREN: WEST OREGON ELEC 34.5KV FEEDER 1, DUTCH CANYON-WARREN SECTION OF ST JOHNS-ST HELENS NO 1 115KV LINE, WARREN-FAIRGROUNDS SECTION OF ST JOHNS-ST HELENS NO 1 115KV LINE, WARREN TAP TO ST JOHNS-ST HELENS NO 1 115KV LINE, TARBELL: COLUMBIA RIVR PUD 115KV FEEDER 1 | LOAD, SOA, NOPE | UNDER REVIEW | DISCONNECT MAINTENANCE ON B-216 AND B-450 | CUSTOMER CONTACT CRPUD KURT NASSHAHN (503-396-1064) OK WITH OUTAGE 10/24/24 CUSTOMER CONTACT WOEC ANDY LARSEN (503-201-3907) OK WITH OUTAGE 10/24/24LONGVIEW OPS TO WORK WITH WOEC TO TRANSFER LOAD AND COLUMBIA RIVER PUD TO PICK UP TERMINAL CLEARANCETHERE'S ONLY A PRIMARY SOURCE FOR STATION SERVICE WITH NO SOURCE OF BACKFEED | Clearance | OUT_OF_SERVICE
25-00444 | 16427363 | 01/21/2025 07:30 | 01/21/2025 15:30 | ALVEY: PCB B-586 |  |  | APPROVED | CUTOVER TO NEW BUS DIFFERENTIAL SET 1 AND DEMO OLD BUS DIFFERENTIAL RELAYS | WORK WILL BE COMPLETED ON 115KV MAIN BUS DIFFERENTIAL RELAY SET 2 AND THIS RELAY WILL BE IN SERVICE BY OUTAGE START DATE.115KV MAIN BUS DIFFERENTIAL RELAY SET 2 WILL REMAIN IN SERVICE FOR THIS WORK. 115KV BUS TIE PCB B-586 WILL BE ISOLATED TO COMPLETE THIS WORK. | Work Permit | OUT_OF_SERVICE
24-00976 | 14881049 | 01/21/2025 07:30 | 01/22/2025 16:00 | CAPTAIN JACK-MALIN NO 2 500KV LINE INCLUDING CAPTAIN JACK: PCB 4924 AND PCB 4986 | CAPTAIN JACK-MALIN NO 2 500KV LINE, CAPTAIN JACK: PCB 4924, CAPTAIN JACK: PCB 4986 | NWACI, SIG, COI | UNDER REVIEW | MOD 4923 AND 4987 COMPLETE SERVICE | * THIS OUTAGE SHOULD BE INCLUDED IN COA. * REQUEST GROUND SWITCHES AT BOTH TERMINALS TO REMAIN OPEN (GROUND SWITCH 8103 AT CAPTAIN JACK, GROUND SWITCH 11L500 AT MALIN). | Clearance | OUT_OF_SERVICE
25-00880 | 16822175 | 01/21/2025 10:00 | 01/21/2025 10:15 | GRAND COULEE: PCB 2392, GRAND COULEE: PCB 2396 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support removing G-23 from service for commutator stoning. |  | Info | OUT_OF_SERVICE
25-00881 | 16834102 | 01/21/2025 14:15 | 01/21/2025 14:30 | GRAND COULEE: PCB 2392, GRAND COULEE: PCB 2396 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support returning G-23 to service after commutator stoning. |  | Info | OUT_OF_SERVICE
25-00985 | 16856671 | 01/22/2025 08:00 | 01/22/2025 14:00 | KERR: PCB B-600 | ELMO-KERR SECTION OF KALISPELL-KERR NO 1 115KV LINE | GEN, LOAD, FLAT, MT-NW | UNDER REVIEW | Test New RAS LLL Indications. Open-Ends KALI-KERR. | No Bypass Disc on B-600. | Work Permit | OUT_OF_SERVICE
25-00690 | 16806269 | 01/23/2025 07:00 | 01/23/2025 15:00 | OLYMPIA: 230KV REACTOR 1 INCLUDING PCB A-349 | OLYMPIA: PCB A-349, OLYMPIA: 230KV REACTOR 1 | NOEL, RP, SOC, WOCN | UNDER REVIEW | TRIP AND IN-SERVICE CHEKCS ON 1/23/2024 BACK TO THE 230kV REACTOR #1 LOR AND PCB A-349. | TRIP AND IN-SERVICE CHEKCS ON 1/23/2024 BACK TO THE 230kV REACTOR #1 LOR AND PCB A-349. | Info | OUT_OF_SERVICE
24-01476 | 14887282 | 01/23/2025 08:00 | 01/23/2025 11:00 | MARION: PCB 4355 |  | NWACI, WOCS, NOPE | UNDER REVIEW | SPC TO PERFORM TRIP CHECKS TO PCB 4355 FROM PEARL 1 500KV LINE RELAYS SETS 1 & 2 OAT |  | Work Permit | OUT_OF_SERVICE
25-00038 | 11036047 | 01/23/2025 09:00 | 01/23/2025 17:00 | DWORSHAK PH: PCB XJ-7 | DWORSHAK PH: PCB XJ-7, DWORSHAK PH: PCB XJ-7 |  | APPROVED | #1468500 XJ-7 NEEDS TO BE OPEN DURING CAPABILITY CURVE TESTING OF UNIT 2 |  | Info | OUT_OF_SERVICE
24-01477 | 14887291 | 01/23/2025 12:00 | 01/23/2025 15:00 | MARION: PCB 4946 |  | NWACI, WOCS, NOPE | UNDER REVIEW | SPC TO PERFORM TRIP CHECKS TO PCB 4368 FROM JDAY 1 500KV LINE RELAYS SETS 1 & 2 OAT |  | Work Permit | OUT_OF_SERVICE
25-00952 | 16840544 | 01/27/2025 07:30 | 02/04/2025 16:30 | KEELER-OREGON CITY NO 2 115KV LINE | KEELER: PCB B-1080, OREGON CITY: PCB B-260 | LOAD, SOA, NOPE | UNDER REVIEW | THEIR PROXIMITY WORK | PGE will cross the BPA line twice with the McLoughlin-Tonquin T-Line line and once with the Sherwood-Wilsonville T-line. Each crossing is adjacent to the Oregon City and Coffee Creek substations. | Clearance | OUT_OF_SERVICE
25-00305 | 16814573 | 01/27/2025 08:00 | 02/02/2025 17:00 | BIG EDDY: THE DALLES PH-BIG EDDY NO. 3 230KV LINE INCLUDING BIG EDDY PCB A-812 | THE DALLES PH-BIG EDDY NO 3 230KV LINE, BIG EDDY: PCB A-812 | GEN, FCRPS, PDCI, WOJD, NWACI | UNDER REVIEW | INSTALL NEW LINE CT FOR GRID MOD PROJECT |  | Clearance | OUT_OF_SERVICE
25-00203 | 16814062 | 01/27/2025 08:00 | 04/07/2025 15:00 | DRISCOLL-KNAPPA SECTION OF DRISCOLL-ASTORIA NO 1 115KV LINE | DRISCOLL: PCB B-2061, DRISCOLL: PCB B-2067 |  | UNDER REVIEW | REBUILD LINE FROM 3/5 TO 12/4 (ISSUED AGAINST DISP TAGS) |  | Clearance | OUT_OF_SERVICE
25-00794 |  | 01/27/2025 08:00 | 03/28/2025 15:00 | BENTON-RINGOLD SECTION OF BENTON-SCOOTENEY NO 1 115KV LINE | CONNELL-SCOOTENEY SECTION OF BENTON-SCOOTENEY NO 1 115KV LINE | TCLA | UNDER REVIEW | COMPLETE LINE REBUILD |  | Clearance | OUT_OF_SERVICE
25-00549 | 16806332 | 01/27/2025 08:00 | 01/27/2025 15:00 | OREGON CITY: 115KV CAP GROUP 1 INCLUDING PCB B-266 | OREGON CITY: 115KV CAP GROUP 1, OREGON CITY: PCB B-266 |  | UNDER REVIEW | PCB ROUTINE SERVICE AND CAP INSPECTION SERVICE |  | Clearance | OUT_OF_SERVICE
25-00491 | 16498048 | 01/28/2025 08:00 | 01/28/2025 15:00 | SCHULTZ: PCB 5160 BFR | SCHULTZ: PCB 5160 | WOCN, NOEL | UNDER REVIEW | RELAY MAINTENANCE, TRIP, AND IN-SERVICE CHECKS. | ISOLATE PCB FOR WORK.NEED TO BRIEFLY CUT OUT AND PERFORM TRIPS TO/FROM THE FOLLOWING LOR'S: RAVER #1, WEST BUS SET #1, AND WEST BUS SET #2.WILL BE CUT OUT LESS THAN 30 MINUTES, PER DSO 355.AFTER PCB 5160 IS BACK IN SERVICE, REQUEST PCB 5157 BE OPENED BRIEFLY TO PUSH CURRENT FOR IN-SERVICE CHECKS. | Work Permit | OUT_OF_SERVICE
25-00609 | 16689482 | 01/28/2025 10:00 | 01/28/2025 10:15 | GRAND COULEE: PCB 2192, GRAND COULEE: PCB 2196 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support removing G-21 from service for commutator stoning. |  | Info | OUT_OF_SERVICE
25-00610 | 16689490 | 01/28/2025 14:15 | 01/28/2025 14:30 | GRAND COULEE: PCB 2192, GRAND COULEE: PCB 2196 |  | GEN, NOH, WOCN | UNDER REVIEW | Bay outage to support returning G-21 to service after commutator stoning. |  | Info | OUT_OF_SERVICE
25-00492 | 16498052 | 01/28/2025 15:00 | 01/28/2025 15:30 | SCHULTZ: PCB 5157 |  | WOCN, NOEL | UNDER REVIEW | OPEN PCB 5157 TO PUSH CURRENT FOR IN-SERVICE CHECKS ON PCB 5160 BFR. TO SUPPORT WORK UNDER FORM 25-00491. |  | Info | OUT_OF_SERVICE
24-11157 | 16073008 | 01/31/2025 16:00 | 01/31/2025 16:30 | CUSTER: PCB 4268 |  | BCHT, BCHW, NOEL, SOC, NI | UNDER REVIEW | IN SERVICE CHECKS | RELATED OUTAGE 24-11120. PCB 4268 OPENED TO FORCE MONE-CUST 1 LINE LOAD THROUGH PCB 4272 FOR IN SERVICE CHECKS. | Info | RELAY_WORK